## Report summary Table
Table 8-2: Market benefits of augmentation options relative to the base case
Augmentation option | 2016-2020 project cost ($M, direct) | Total lifecycle project cost (2016-2030) ($M, direct) | NPV of net economic benefit ($M) | Project ranking | offset
Base Case - Do Nothing | 0 | 0 | 0 | 12 | 0
Option 1a - Upgrade 11 kV transformer cables and 11 kV switchboards and install a third 11 kV switchboard (in new switch-room building) in 2018 | 10.2282 | 16.7066 | 802.6984 | 5 | 5
Option 1b - Upgrade 11 kV transformer cables and 11 kV switchboards and install a third 11 kV switchboard (in existing switch-room building) in 2018 | 6.5324 | 12.6003 | 806.8048 | 1 | 10
Option 1c - Upgrade 11 kV transformer cables and 11 kV switchboards (in new switch-room building) in 2018 | 8.5959 | 16.9474 | 802.4577 | 6 | 15
Option 1d - Upgrade 11 kV transformer cables and 11 kV switchboards (in existing switch-room building) in 2018 | 4.958 | 12.9053 | 806.4998 | 2 | 20
Option 2 - Rebuild Flemington Zone Substation in 2018 | 15.9061 | 19.7275 | 799.6776 | 7 | 25
Option 3 - Establish a new zone substation to upgrade FT in 2018 | 41.0301 | 45.5882 | 773.8169 | 9 | 30
Option 4 - Install a third 66/11 kV transformer (in existing switch-room building) in 2018 | 6.3304 | 16.4845 | 802.9171 | 4 | 35
Option 5a - Enrol DSM of 7.25 MVA in 2018, with commissioning of network Option 1b delayed to 2019 | 7.7872 | 13.8551 | 805.5291 | 3 | 40
Option 5b - Install 7.25 MVAh of battery storage in 2018, with commissioning of network Option 1b delayed to 2019 | 12.9415 | 19.0094 | 797.0771 | 8 | 45
Option 6 - Upgrade 11 kV transformer cables (in existing switch-room building) in 2018 | 1.1683 | 12.8032 | 623.209 | 10 | 50
Option 7 - Upgrade 11 kV transformer cables and 11 kV transformer circuit breakers (in existing switch-room building) in 2018 | 1.4877 | 13.1581 | 622.8541 | 11 | 55

## Sensitivity Analysis Summary
Option | Net Economic Benefit ($) | Rank | Net Economic Benefit ($) | Rank | Net Economic Benefit ($) | Rank | Net Economic Benefit ($) | Rank | Net Economic Benefit ($) | Rank | Net Economic Benefit ($) | Rank | Option Selection | Average Net Economic benefit ($) | Overall Rank of Feasible Options | Include Option in Ranking?
| Base (planning) scenario |  | VCR High (+20%) |  | VCR Low (-20%) |  | Discount Rate High (8.26%) |  | Investment Cost High (+30%) |  | Investment Cost Low (-30%)
Do Nothing | 0 | 12 | 0 | 12 | 0 | 12 | 0 | 12 | 0 | 12 | 0 | 12 |  | 0 | 12 | yes
Option 1a | 802698387.5746 | 5 | 966579395.0065 | 5 | 638817380.1427 | 5 | 675771334.1382 | 5 | 797686392.6992 | 5 | 807710382.45 | 5 |  | 781543878.6685 | 5 | yes
Option 1b | 806804756.3166 | 1 | 970685763.7485 | 1 | 642923748.8847 | 1 | 679686297.3858 | 1 | 803024672.0637 | 1 | 810584840.5694 | 2 | Proposed preferred option | 785618346.4948 | 1 | yes
Option 1c | 802457682.4153 | 6 | 966338689.8471 | 6 | 638576674.9834 | 6 | 675634380.6161 | 6 | 797373475.992 | 6 | 807541888.8385 | 6 |  | 781320465.4487 | 6 | yes
Option 1d | 806499766.4217 | 2 | 970380773.8536 | 2 | 642618758.9898 | 2 | 679488055.5595 | 2 | 802628185.2004 | 2 | 811378642.2092 | 1 |  | 785499030.3724 | 2 | yes
Option 2 | 799677556.8427 | 7 | 963558564.2746 | 7 | 635796549.4109 | 7 | 672065459.9912 | 7 | 793759312.7477 | 7 | 805595800.9377 | 7 |  | 778408874.0342 | 7 | yes
Option 3 | 773816880.3049 | 9 | 937697887.7367 | 9 | 609935872.873 | 9 | 647317665.8254 | 9 | 760140433.2485 | 9 | 787493327.3612 | 9 |  | 752733677.8916 | 9 | yes
Option 4 | 802917121.5903 | 4 | 966797444.9846 | 4 | 639036798.1961 | 4 | 676165314.6486 | 4 | 797971772.976 | 4 | 807862470.2046 | 4 |  | 781791820.4334 | 4 | yes
Option 5a | 805529071.7234 | 3 | 969405896.2326 | 3 | 641652247.2142 | 3 | 678556380.2814 | 3 | 801372556.4766 | 3 | 809685586.9702 | 3 |  | 784366956.4831 | 3 | yes
Option 5b | 797077081.4046 | 8 | 960294379.9147 | 8 | 633859782.8944 | 8 | 670414201.4874 | 8 | 791374258.0607 | 8 | 802779904.7484 | 8 |  | 775966601.4184 | 8 | yes
Option 6 | 623209029.7959 | 10 | 750411474.5301 | 10 | 496006585.0618 | 10 | 522816410.5566 | 10 | 619368071.6335 | 10 | 627049987.9584 | 10 |  | 606476926.5894 | 10 | yes
Option 7 | 622854100.9535 | 11 | 750056545.6876 | 11 | 495651656.2194 | 11 | 522478025.6085 | 11 | 618906664.1383 | 11 | 626801537.7687 | 11 |  | 606124755.0627 | 11 | yes

## Opt 1b - cost-benefit timing
Do Nothing |  |  |  | Base (Do Nothing) Risk ($) | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Cost of expected unserved energy ($) |  | 826901874.4102 |  |  | 2784207.75 | 5012824 | 8838504 | 15275112 | 25371752 | 40374728 | 62129832 | 92754992 | 134675768 | 190223064 | 190223064 | 190223064 | 190223064 | 190223064 | 190223064
Discount Rate | 6.37%
Option 1a |  |  |  | Residual (Option 5b) Risk ($) | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
N - 1 Limit |  |  |  |  | 3000 | 3597.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
N Limit |  |  |  |  | 2781207.75 | 942.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total |  |  |  |  | 2784207.75 | 4539.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Benefit |  | 824113398.9344 |  | Annualised benefits ($) | 0 | 5008284.42 | 8838504 | 15275112 | 25371752 | 40374728 | 62129832 | 92754992 | 134675768 | 190223064 | 190223064 | 190223064 | 190223064 | 190223064 | 190223064
Net economic benefit |  | 811513118.0915 |  | $M | 0 | 5.0083 | 8.8385 | 15.2751 | 25.3718 | 40.3747 | 62.1298 | 92.755 | 134.6758 | 190.2231 | 190.2231 | 190.2231 | 190.2231 | 190.2231 | 190.2231
|  | 0 | 6532413.9641 | Annualised costs ($) | 0 | 435999.8992 | 435999.8992 | 435999.8992 | 435999.8992 | 435999.8992 | 435999.8992 | 435999.8992 | 435999.8992 | 435999.8992 | 435999.8992 | 435999.8992 | 435999.8992 | 435999.8992 | 435999.8992
|  |  |  | $M | 0 | 0.436 | 0.436 | 0.436 | 0.436 | 0.436 | 0.436 | 0.436 | 0.436 | 0.436 | 0.436 | 0.436 | 0.436 | 0.436 | 0.436
| Option costs ($M 2016 Real) |  | Option costs ($M 2016 Real)
| 2016-2020 | 2016-2030 | 2016-2020 | 2016-2030 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Option 1a | 6.5324 | 12.6003 | 6532413.9641 | 12600280.8428 | 0 | 0 | 7187159.4161 | 110502.576 | 113265.1404 | 116096.7689 | 118999.1882 | 121974.1679 | 125023.5221 | 128149.1101 | 131352.8379 | 134636.6588 | 138002.5753 | 141452.6397 | 12826943.8754
Capital | 6.3521 | 11.6943 | 6352123.8838 | 11694297.2241 | 0 | 0 | 7187159.4161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12681954.9197
Operational | 0.18029 | 0.90598 | 180290.0803 | 905983.6187 | 0 | 0 | 0 | 110502.576 | 113265.1404 | 116096.7689 | 118999.1882 | 121974.1679 | 125023.5221 | 128149.1101 | 131352.8379 | 134636.6588 | 138002.5753 | 141452.6397 | 144988.9557
Network option Capital | 6.3521 | 11.6943 | 6352123.8838 | 11694297.2241 | 0 | 0 | 7187159.4161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12681954.9197
Network option O&M | 0.18029 | 0.90598 | 180290.0803 | 905983.6187 | 0 | 0 | 0 | 110502.576 | 113265.1404 | 116096.7689 | 118999.1882 | 121974.1679 | 125023.5221 | 128149.1101 | 131352.8379 | 134636.6588 | 138002.5753 | 141452.6397 | 144988.9557

## Option Costs
Year |  |  |  |  | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Discount Rate |  |  | 6.37%
Inflation Rate |  |  | 2.5%
O&M |  |  | 1.5%
| Option costs ($M 2016 Real) |  | Option costs ($2016 Real)
| 2016-2020 | 2016-2030 | 2016-2020 | 2016-2030
Option 1a | 10.2282 | 16.7066 | 10228212.146 | 16706649.5848 | 0 | 0 | 11253388.3553 | 173020.846 | 177346.3671 | 181780.0263 | 186324.5269 | 190982.6401 | 195757.2061 | 200651.1363 | 205667.4147 | 210809.1001 | 216079.3276 | 221481.3107 | 12908973.2632
Capital | 9.9459 | 15.2881 | 9945920.6073 | 15288093.9477 | 0 | 0 | 11253388.3553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12681954.9197
Operational | 0.28229 | 1.4186 | 282291.5386 | 1418555.6371 | 0 | 0 | 0 | 173020.846 | 177346.3671 | 181780.0263 | 186324.5269 | 190982.6401 | 195757.2061 | 200651.1363 | 205667.4147 | 210809.1001 | 216079.3276 | 221481.3107 | 227018.3435
Option 1b | 6.5324 | 12.6003 | 6532413.9641 | 12600280.8428 | 0 | 0 | 7187159.4161 | 110502.576 | 113265.1404 | 116096.7689 | 118999.1882 | 121974.1679 | 125023.5221 | 128149.1101 | 131352.8379 | 134636.6588 | 138002.5753 | 141452.6397 | 12826943.8754
Capital | 6.3521 | 11.6943 | 6352123.8838 | 11694297.2241 | 0 | 0 | 7187159.4161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12681954.9197
Operational | 0.18029 | 0.90598 | 180290.0803 | 905983.6187 | 0 | 0 | 0 | 110502.576 | 113265.1404 | 116096.7689 | 118999.1882 | 121974.1679 | 125023.5221 | 128149.1101 | 131352.8379 | 134636.6588 | 138002.5753 | 141452.6397 | 144988.9557
Option 1c | 8.5959 | 16.9474 | 8595928.6329 | 16947354.7441 | 0 | 0 | 9457500.6658 | 145409.0727 | 149044.2996 | 2666937.4082 | 195244.9849 | 200126.1095 | 205129.2622 | 210257.4938 | 215513.9311 | 220901.7794 | 226424.3239 | 232084.932 | 12919841.975
Capital | 8.3587 | 15.5471 | 8358686.9835 | 15547143.5571 | 0 | 0 | 9457500.6658 | 0 | 0 | 2514167.0012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12681954.9197
Operational | 0.23724 | 1.4002 | 237241.6494 | 1400211.1871 | 0 | 0 | 0 | 145409.0727 | 149044.2996 | 152770.407 | 195244.9849 | 200126.1095 | 205129.2622 | 210257.4938 | 215513.9311 | 220901.7794 | 226424.3239 | 232084.932 | 237887.0553
Option 1d | 4.958 | 12.9053 | 4957987.7512 | 12905270.7377 | 0 | 0 | 5454928.0782 | 83869.5192 | 85966.2572 | 2602282.4148 | 128973.6166 | 132197.957 | 135502.9059 | 138890.4786 | 142362.7405 | 145921.8091 | 149569.8543 | 153309.1006 | 12839096.7479
Capital | 4.8212 | 12.0096 | 4821150.7389 | 12009607.3124 | 0 | 0 | 5454928.0782 | 0 | 0 | 2514167.0012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12681954.9197
Operational | 0.13684 | 0.89566 | 136837.0123 | 895663.4253 | 0 | 0 | 0 | 83869.5192 | 85966.2572 | 88115.4136 | 128973.6166 | 132197.957 | 135502.9059 | 138890.4786 | 142362.7405 | 145921.8091 | 149569.8543 | 153309.1006 | 157141.8282
Option 2 | 15.9061 | 19.7275 | 15906128.8223 | 19727480.3167 | 0 | 0 | 17500404.0111 | 269068.7117 | 275795.4295 | 2796857.3164 | 328412.8907 | 336623.213 | 345038.7933 | 353664.7631 | 362506.3822 | 371569.0418 | 380858.2678 | 390379.7245 | 400139.2176
Capital | 15.4671 | 17.3134 | 15467130.7339 | 17313413.9671 | 0 | 0 | 17500404.0111 | 0 | 0 | 2514167.0012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Operational | 0.439 | 2.4141 | 438998.0883 | 2414066.3496 | 0 | 0 | 0 | 269068.7117 | 275795.4295 | 282690.3152 | 328412.8907 | 336623.213 | 345038.7933 | 353664.7631 | 362506.3822 | 371569.0418 | 380858.2678 | 390379.7245 | 400139.2176
Option 3 | 41.0301 | 45.5882 | 41030077.3763 | 45588156.8546 | 0 | 0 | 45142532.0842 | 694066.4308 | 711418.0916 | 729203.5439 | 747433.6324 | 766119.4733 | 785272.4601 | 804904.2716 | 825026.8784 | 845652.5503 | 866793.8641 | 888463.7107 | 910675.3035
Capital | 39.8977 | 39.8977 | 39897675.7886 | 39897675.7886 | 0 | 0 | 45142532.0842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Operational | 1.1324 | 5.6905 | 1132401.5877 | 5690481.0659 | 0 | 0 | 0 | 694066.4308 | 711418.0916 | 729203.5439 | 747433.6324 | 766119.4733 | 785272.4601 | 804904.2716 | 825026.8784 | 845652.5503 | 866793.8641 | 888463.7107 | 910675.3035
Option 4 | 6.3304 | 16.4845 | 6330425.6878 | 16484495.381 | 0 | 0 | 6964925.8054 | 107085.7343 | 109762.8776 | 5140840.952 | 192630.2586 | 197446.015 | 202382.1654 | 207441.7196 | 212627.7625 | 217943.4566 | 223392.043 | 228976.8441 | 12916656.1849
Capital | 6.1557 | 15.1905 | 6155710.3434 | 15190450.15 | 0 | 0 | 6964925.8054 | 0 | 0 | 5028334.0024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12681954.9197
Operational | 0.17472 | 1.294 | 174715.3444 | 1294045.231 | 0 | 0 | 0 | 107085.7343 | 109762.8776 | 112506.9496 | 192630.2586 | 197446.015 | 202382.1654 | 207441.7196 | 212627.7625 | 217943.4566 | 223392.043 | 228976.8441 | 234701.2652
Option 5a | 7.7872 | 13.8551 | 7787183.944 | 13855050.8228 | 0 | 0 | 1785090.625 | 7366838.4015 | 113265.1404 | 116096.7689 | 118999.1882 | 121974.1679 | 125023.5221 | 128149.1101 | 131352.8379 | 134636.6588 | 138002.5753 | 141452.6397 | 12826943.8754
Capital | 6.2557 | 11.5978 | 6255659.1529 | 11597832.4932 | 0 | 0 | 152340.625 | 7366838.4015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12681954.9197
Operational | 1.5315 | 2.2572 | 1531524.7911 | 2257218.3295 | 0 | 0 | 1632750 | 0 | 113265.1404 | 116096.7689 | 118999.1882 | 121974.1679 | 125023.5221 | 128149.1101 | 131352.8379 | 134636.6588 | 138002.5753 | 141452.6397 | 144988.9557
Option 5b | 12.9415 | 19.0094 | 12941544.2674 | 19009411.1462 | 0 | 0 | 7617031.25 | 7366838.4015 | 113265.1404 | 116096.7689 | 118999.1882 | 121974.1679 | 125023.5221 | 128149.1101 | 131352.8379 | 134636.6588 | 138002.5753 | 141452.6397 | 12826943.8754
Capital | 12.8531 | 18.1952 | 12853069.459 | 18195242.7994 | 0 | 0 | 7617031.25 | 7366838.4015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12681954.9197
Operational | 0.088475 | 0.81417 | 88474.8084 | 814168.3468 | 0 | 0 | 0 | 0 | 113265.1404 | 116096.7689 | 118999.1882 | 121974.1679 | 125023.5221 | 128149.1101 | 131352.8379 | 134636.6588 | 138002.5753 | 141452.6397 | 144988.9557
Option 6 | 1.1683 | 12.8032 | 1168272.8389 | 12803193.8748 | 0 | 0 | 1285369.1118 | 19762.5501 | 20256.6138 | 7563264.0328 | 137248.0579 | 140679.2593 | 144196.2408 | 147801.1468 | 151496.1755 | 155283.5799 | 159165.6694 | 163144.8111 | 12849178.3511
Capital | 1.136 | 12.0171 | 1136029.3214 | 12017052.3613 | 0 | 0 | 1285369.1118 | 0 | 0 | 7542501.0036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12681954.9197
Operational | 0.032244 | 0.78614 | 32243.5175 | 786141.5135 | 0 | 0 | 0 | 19762.5501 | 20256.6138 | 20763.0292 | 137248.0579 | 140679.2593 | 144196.2408 | 147801.1468 | 151496.1755 | 155283.5799 | 159165.6694 | 163144.8111 | 167223.4314
Option 7 | 1.4877 | 13.1581 | 1487714.5289 | 13158122.7172 | 0 | 0 | 1636828.5206 | 25166.2385 | 25795.3945 | 7568941.2829 | 143067.2392 | 146643.9202 | 150310.0182 | 154067.7687 | 157919.4629 | 161867.4495 | 165914.1357 | 170061.9891 | 12856268.4585
Capital | 1.4467 | 12.3277 | 1446654.643 | 12327677.6829 | 0 | 0 | 1636828.5206 | 0 | 0 | 7542501.0036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12681954.9197
Operational | 0.04106 | 0.83045 | 41059.8859 | 830445.0344 | 0 | 0 | 0 | 25166.2385 | 25795.3945 | 26440.2793 | 143067.2392 | 146643.9202 | 150310.0182 | 154067.7687 | 157919.4629 | 161867.4495 | 165914.1357 | 170061.9891 | 174313.5388
|  | Real $2015 |  |  | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
cables (existing building) |  | 1193593 |  |  | 1223432.825 | 1254018.6456 | 1285369.1118 | 1317503.3396 | 1350440.923 | 1384201.9461 | 1418806.9948 | 1454277.1696 | 1490634.0989 | 1527899.9514 | 1566097.4501 | 1605249.8864 | 1645381.1336 | 1686515.6619 | 1728678.5534
cables and CBs (existing building) |  | 1519958 |  |  | 1557956.95 | 1596905.8737 | 1636828.5206 | 1677749.2336 | 1719692.9644 | 1762685.2886 | 1806752.4208 | 1851921.2313 | 1898219.2621 | 1945674.7436 | 1994316.6122 | 2044174.5275 | 2095278.8907 | 2147660.863 | 2201352.3846
cables and two switchboards (existing building) |  | 5065443 |  |  | 5192079.075 | 5321881.0519 | 5454928.0782 | 5591301.2801 | 5731083.8121 | 5874360.9074 | 6021219.9301 | 6171750.4284 | 6326044.1891 | 6484195.2938 | 6646300.1762 | 6812457.6806 | 6982769.1226 | 7157338.3506 | 7336271.8094
cables and three switchboards (existing building) |  | 6673992 |  |  | 6840841.8 | 7011862.845 | 7187159.4161 | 7366838.4015 | 7551009.3616 | 7739784.5956 | 7933279.2105 | 8131611.1908 | 8334901.4705 | 8543274.0073 | 8756855.8575 | 8975777.2539 | 9200171.6853 | 9430175.9774 | 9665930.3768
3rd transformer (existing building) |  | 6467626 |  |  | 6629316.65 | 6795049.5662 | 6964925.8054 | 7139048.9505 | 7317525.1743 | 7500463.3037 | 7687974.8863 | 7880174.2584 | 8077178.6149 | 8279108.0802 | 8486085.7822 | 8698237.9268 | 8915693.875 | 9138586.2218 | 9367050.8774
cables, transformers and two switchboards (existing building) |  | 12811709.3963 |  |  | 13132002.1312 | 13460302.1845 | 13796809.7391 | 14141729.9826 | 14495273.2322 | 14857655.063 | 15229096.4395 | 15609823.8505 | 16000069.4468 | 16400071.183 | 16810072.9625 | 17230324.7866 | 17661082.9063 | 18102609.9789 | 18555175.2284
cables, transformers and two switchboards (new building) |  | 16250864.8556 |  |  | 16657136.477 | 17073564.8889 | 17500404.0111 | 17937914.1114 | 18386361.9642 | 18846021.0133 | 19317171.5386 | 19800100.8271 | 20295103.3478 | 20802480.9315 | 21322542.9548 | 21855606.5286 | 22401996.6918 | 22962046.6091 | 23536097.7744
cables and three switchboards (new building) |  | 10449889.7976 |  |  | 10711137.0425 | 10978915.4686 | 11253388.3553 | 11534723.0642 | 11823091.1408 | 12118668.4193 | 12421635.1298 | 12732176.008 | 13050480.4082 | 13376742.4184 | 13711160.9789 | 14053940.0033 | 14405288.5034 | 14765420.716 | 15134556.2339
new cables, 2 switchboards (new building) |  | 8782229.5471 |  |  | 9001785.2857 | 9226829.9179 | 9457500.6658 | 9693938.1825 | 9936286.637 | 10184693.803 | 10439311.148 | 10700293.9267 | 10967801.2749 | 11241996.3068 | 11523046.2145 | 11811122.3698 | 12106400.4291 | 12409060.4398 | 12719286.9508
new zone substation (at alternative site) |  | 41919328.7008 |  |  | 42967311.9183 | 44041494.7163 | 45142532.0842 | 46271095.3863 | 47427872.7709 | 48613569.5902 | 49828908.83 | 51074631.5507 | 52351497.3395 | 53660284.773 | 55001791.8923 | 56376836.6896 | 57786257.6069 | 59230914.047 | 60711686.8982
install three new switchboards (existing building) |  | 6503874.9769 |  |  | 6666471.8513 | 6833133.6476 | 7003961.9888 | 7179061.0385 | 7358537.5645 | 7542501.0036 | 7731063.5287 | 7924340.1169 | 8122448.6198 | 8325509.8353 | 8533647.5812 | 8746988.7707 | 8965663.49 | 9189805.0773 | 9419550.2042
install two new switchboards (existing building) |  | 4335916.6513 |  |  | 4444314.5676 | 4555422.4317 | 4669307.9925 | 4786040.6923 | 4905691.7097 | 5028334.0024 | 5154042.3525 | 5282893.4113 | 5414965.7466 | 5550339.8902 | 5689098.3875 | 5831325.8472 | 5977108.9933 | 6126536.7182 | 6279700.1361
install one new switchboards (existing building) |  | 2167958.3256 |  |  | 2222157.2838 | 2277711.2159 | 2334653.9963 | 2393020.3462 | 2452845.8548 | 2514167.0012 | 2577021.1762 | 2641446.7056 | 2707482.8733 | 2775169.9451 | 2844549.1937 | 2915662.9236 | 2988554.4967 | 3063268.3591 | 3139850.0681
Replace two transformers (existing building) |  | 8756453.0654 |  |  | 8975364.3921 | 9199748.5019 | 9429742.2144 | 9665485.7698 | 9907122.914 | 10154800.9869 | 10408671.0116 | 10668887.7868 | 10935609.9815 | 11209000.2311 | 11489225.2368 | 11776455.8678 | 12070867.2644 | 12372638.9461 | 12681954.9197
DM capital setup cost |  | 141463.4146 |  |  | 145000 | 148625 | 152340.625 | 156149.1406 | 160052.8691 | 164054.1909 | 168155.5456 | 172359.4343 | 176668.4201 | 181085.1306 | 185612.2589 | 190252.5654 | 195008.8795 | 199884.1015 | 204881.204
Battery energy storage solution (7.25 MVAh) |  | 7073170.7317 |  |  | 7250000 | 7431250 | 7617031.25 | 7807457.0312 | 8002643.457 | 8202709.5435 | 8407777.282 | 8617971.7141 | 8833421.0069 | 9054256.5321 | 9280612.9454 | 9512628.2691 | 9750443.9758 | 9994205.0752 | 10244060.2021
Battery energy storage solution (0.50 MVAh) |  | 487804.878 |  |  | 500000 | 512500 | 525312.5 | 538445.3125 | 551906.4453 | 565704.1064 | 579846.7091 | 594342.8768 | 609201.4488 | 624431.485 | 640042.2721 | 656043.3289 | 672444.4121 | 689255.5224 | 706486.9105

## Cost-Benefit (BASE)
VCR | 39440 |  |  | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Discount Rate | 6.37% |  | Option costs ($2016 Real)
2016-2030
Do Nothing
Weighted EUSE (MVAh) |  |  |  | 70.6 | 127.1 | 224.1 | 387.3 | 643.3 | 1023.7 | 1575.3 | 2351.8 | 3414.7 | 4823.1 | 4823.1 | 4823.1 | 4823.1 | 4823.1 | 4823.1
Weighted Cost of EUSE |  | 47818992.3118 | 826901874.4102 | 2784207.75 | 5012824 | 8838504 | 15275112 | 25371752 | 40374728 | 62129832 | 92754992 | 134675768 | 190223064 | 190223064 | 190223064 | 190223064 | 190223064 | 190223064
Benefits |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Costs |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Net Economic Benefit |  | 0 | 0
Option 1a
Weighted EUSE (MVAh) |  |  |  | 70.6 | 127.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Cost of EUSE |  | 7496837.2508 | 7496837.2508 | 2784207.75 | 5012824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Benefits |  | 40322155.061 | 819405037.1594 | 0 | 0 | 8838504 | 15275112 | 25371752 | 40374728 | 62129832 | 92754992 | 134675768 | 190223064 | 190223064 | 190223064 | 190223064 | 190223064 | 190223064
Costs |  | 10228212.146 | 16706649.5848 | 0 | 0 | 11253388.3553 | 173020.846 | 177346.3671 | 181780.0263 | 186324.5269 | 190982.6401 | 195757.2061 | 200651.1363 | 205667.4147 | 210809.1001 | 216079.3276 | 221481.3107 | 12908973.2632
Net Economic Benefit |  | 0 | 802698387.5746
Option 1b
Weighted EUSE (MVAh) |  |  |  | 70.6 | 127.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Cost of EUSE |  | 7496837.2508 | 7496837.2508 | 2784207.75 | 5012824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Benefits |  | 40322155.061 | 819405037.1594 | 0 | 0 | 8838504 | 15275112 | 25371752 | 40374728 | 62129832 | 92754992 | 134675768 | 190223064 | 190223064 | 190223064 | 190223064 | 190223064 | 190223064
Costs |  | 6532413.9641 | 12600280.8428 | 0 | 0 | 7187159.4161 | 110502.576 | 113265.1404 | 116096.7689 | 118999.1882 | 121974.1679 | 125023.5221 | 128149.1101 | 131352.8379 | 134636.6588 | 138002.5753 | 141452.6397 | 12826943.8754
Net Economic Benefit |  | 0 | 806804756.3166
Option 1c
Weighted EUSE (MVAh) |  |  |  | 70.6 | 127.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Cost of EUSE |  | 7496837.2508 | 7496837.2508 | 2784207.75 | 5012824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Benefits |  | 40322155.061 | 819405037.1594 | 0 | 0 | 8838504 | 15275112 | 25371752 | 40374728 | 62129832 | 92754992 | 134675768 | 190223064 | 190223064 | 190223064 | 190223064 | 190223064 | 190223064
Costs |  | 8595928.6329 | 16947354.7441 | 0 | 0 | 9457500.6658 | 145409.0727 | 149044.2996 | 2666937.4082 | 195244.9849 | 200126.1095 | 205129.2622 | 210257.4938 | 215513.9311 | 220901.7794 | 226424.3239 | 232084.932 | 12919841.975
Net Economic Benefit |  | 0 | 802457682.4153
Option 1d
Weighted EUSE (MVAh) |  |  |  | 70.6 | 127.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Cost of EUSE |  | 7496837.2508 | 7496837.2508 | 2784207.75 | 5012824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Benefits |  | 40322155.061 | 819405037.1594 | 0 | 0 | 8838504 | 15275112 | 25371752 | 40374728 | 62129832 | 92754992 | 134675768 | 190223064 | 190223064 | 190223064 | 190223064 | 190223064 | 190223064
Costs |  | 4957987.7512 | 12905270.7377 | 0 | 0 | 5454928.0782 | 83869.5192 | 85966.2572 | 2602282.4148 | 128973.6166 | 132197.957 | 135502.9059 | 138890.4786 | 142362.7405 | 145921.8091 | 149569.8543 | 153309.1006 | 12839096.7479
Net Economic Benefit |  | 0 | 806499766.4217
Option 2
Weighted EUSE (MVAh) |  |  |  | 70.6 | 127.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Cost of EUSE |  | 7496837.2508 | 7496837.2508 | 2784207.75 | 5012824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Benefits |  | 40322155.061 | 819405037.1594 | 0 | 0 | 8838504 | 15275112 | 25371752 | 40374728 | 62129832 | 92754992 | 134675768 | 190223064 | 190223064 | 190223064 | 190223064 | 190223064 | 190223064
Costs |  | 15906128.8223 | 19727480.3167 | 0 | 0 | 17500404.0111 | 269068.7117 | 275795.4295 | 2796857.3164 | 328412.8907 | 336623.213 | 345038.7933 | 353664.7631 | 362506.3822 | 371569.0418 | 380858.2678 | 390379.7245 | 400139.2176
Net Economic Benefit |  | 0 | 799677556.8427
Option 3
Weighted EUSE (MVAh) |  |  |  | 70.6 | 127.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Cost of EUSE |  | 7496837.2508 | 7496837.2508 | 2784207.75 | 5012824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Benefits |  | 40322155.061 | 819405037.1594 | 0 | 0 | 8838504 | 15275112 | 25371752 | 40374728 | 62129832 | 92754992 | 134675768 | 190223064 | 190223064 | 190223064 | 190223064 | 190223064 | 190223064
Costs |  | 41030077.3763 | 45588156.8546 | 0 | 0 | 45142532.0842 | 694066.4308 | 711418.0916 | 729203.5439 | 747433.6324 | 766119.4733 | 785272.4601 | 804904.2716 | 825026.8784 | 845652.5503 | 866793.8641 | 888463.7107 | 910675.3035
Net Economic Benefit |  | 0 | 773816880.3049
Option 4
Weighted EUSE (MVAh) |  |  |  | 70.6 | 127.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Cost of EUSE |  | 7496930.5021 | 7500257.4389 | 2784207.75 | 5012824 | 0 | 0 | 119.38 | 260.83 | 264.37 | 382.32 | 662.97 | 775.58 | 775.58 | 775.58 | 775.58 | 775.58 | 775.58
Benefits |  | 40322061.8097 | 819401616.9713 | 0 | 0 | 8838504 | 15275112 | 25371632.62 | 40374467.17 | 62129567.63 | 92754609.68 | 134675105.03 | 190222288.42 | 190222288.42 | 190222288.42 | 190222288.42 | 190222288.42 | 190222288.42
Costs |  | 6330425.6878 | 16484495.381 | 0 | 0 | 6964925.8054 | 107085.7343 | 109762.8776 | 5140840.952 | 192630.2586 | 197446.015 | 202382.1654 | 207441.7196 | 212627.7625 | 217943.4566 | 223392.043 | 228976.8441 | 12916656.1849
Net Economic Benefit |  | 0 | 802917121.5903
Option 5a
Weighted EUSE (MVAh) |  |  |  | 70.6 | 127.1 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Cost of EUSE |  | 7517751.8641 | 7517751.8641 | 2784207.75 | 5012824 | 23664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Benefits |  | 40301240.4477 | 819384122.5462 | 0 | 0 | 8814840 | 15275112 | 25371752 | 40374728 | 62129832 | 92754992 | 134675768 | 190223064 | 190223064 | 190223064 | 190223064 | 190223064 | 190223064
Costs |  | 7787183.944 | 13855050.8228 | 0 | 0 | 1785090.625 | 7366838.4015 | 113265.1404 | 116096.7689 | 118999.1882 | 121974.1679 | 125023.5221 | 128149.1101 | 131352.8379 | 134636.6588 | 138002.5753 | 141452.6397 | 12826943.8754
Net Economic Benefit |  | 0 | 805529071.7234
Option 5b
Weighted EUSE (MVAh) |  |  |  | 70.6 | 70.4 | 124.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Cost of EUSE |  | 10815381.8594 | 10815381.8594 | 2784207.75 | 3941364.77 | 4894504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Benefits |  | 37003610.4523 | 816086492.5508 | 0 | 1071459.23 | 3944000 | 15275112 | 25371752 | 40374728 | 62129832 | 92754992 | 134675768 | 190223064 | 190223064 | 190223064 | 190223064 | 190223064 | 190223064
Costs |  | 12941544.2674 | 19009411.1462 | 0 | 0 | 7617031.25 | 7366838.4015 | 113265.1404 | 116096.7689 | 118999.1882 | 121974.1679 | 125023.5221 | 128149.1101 | 131352.8379 | 134636.6588 | 138002.5753 | 141452.6397 | 12826943.8754
Net Economic Benefit |  | 0 | 797077081.4046
Option 6
Weighted EUSE (MVAh) |  |  |  | 70.6 | 127.1 | 223.9 | 386.9 | 642.6 | 1022.6 | 1573.6 | 2349.2 | 3410.8 | 4817.4 | 4817.4 | 4817.4 | 4817.4 | 4817.4 | 4817.4
Weighted Cost of EUSE |  | 29271708.8068 | 190889650.7395 | 2784207.75 | 3941364.77 | 5875532.49 | 8482238.31 | 13495176.12 | 16928845.79 | 17443241.34 | 22320679.38 | 28953478.32 | 35400321.6 | 35400321.6 | 35400321.6 | 35400321.6 | 35400321.6 | 35400321.6
Benefits |  | 18547283.505 | 636012223.6707 | 0 | 1071459.23 | 2962971.51 | 6792873.69 | 11876575.88 | 23445882.21 | 44686590.66 | 70434312.62 | 105722289.68 | 154822742.4 | 154822742.4 | 154822742.4 | 154822742.4 | 154822742.4 | 154822742.4
Costs |  | 1168272.8389 | 12803193.8748 | 0 | 0 | 1285369.1118 | 19762.5501 | 20256.6138 | 7563264.0328 | 137248.0579 | 140679.2593 | 144196.2408 | 147801.1468 | 151496.1755 | 155283.5799 | 159165.6694 | 163144.8111 | 12849178.3511
Net Economic Benefit |  | 0 | 623209029.7959
Option 7
Weighted EUSE (MVAh) |  |  |  | 70.6 | 127.1 | 223.9 | 386.9 | 642.6 | 1022.6 | 1573.6 | 2349.2 | 3410.8 | 4817.4 | 4817.4 | 4817.4 | 4817.4 | 4817.4 | 4817.4
Weighted Cost of EUSE |  | 29271708.8068 | 190889650.7395 | 2784207.75 | 3941364.77 | 5875532.49 | 8482238.31 | 13495176.12 | 16928845.79 | 17443241.34 | 22320679.38 | 28953478.32 | 35400321.6 | 35400321.6 | 35400321.6 | 35400321.6 | 35400321.6 | 35400321.6
Benefits |  | 18547283.505 | 636012223.6707 | 0 | 1071459.23 | 2962971.51 | 6792873.69 | 11876575.88 | 23445882.21 | 44686590.66 | 70434312.62 | 105722289.68 | 154822742.4 | 154822742.4 | 154822742.4 | 154822742.4 | 154822742.4 | 154822742.4
Costs |  | 1487714.5289 | 13158122.7172 | 0 | 0 | 1636828.5206 | 25166.2385 | 25795.3945 | 7568941.2829 | 143067.2392 | 146643.9202 | 150310.0182 | 154067.7687 | 157919.4629 | 161867.4495 | 165914.1357 | 170061.9891 | 12856268.4585
Net Economic Benefit |  | 0 | 622854100.9535

## Cost-Benefit (VCR+20%)
VCR | 47328 |  | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Discount Rate | 6.37%
Option costs ($2016 Real)
Do Nothing
Weighted EUSE (MVAh) |  |  | 70.6 | 127.1 | 224.1 | 387.3 | 643.3 | 1023.7 | 1575.3 | 2351.8 | 3414.7 | 4823.1 | 4823.1 | 4823.1 | 4823.1 | 4823.1 | 4823.1
Weighted Cost of EUSE |  | 992282249.2923 | 3341049.3 | 6015388.8 | 10606204.8 | 18330134.4 | 30446102.4 | 48449673.6 | 74555798.4 | 111305990.4 | 161610921.6 | 228267676.8 | 228267676.8 | 228267676.8 | 228267676.8 | 228267676.8 | 228267676.8
Benefits |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Costs |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Net Economic Benefit |  | 0
Option 1a
Weighted EUSE (MVAh) |  |  | 70.6 | 127.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Cost of EUSE |  | 8996204.701 | 3341049.3 | 6015388.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Benefits |  | 983286044.5913 | 0 | 0 | 10606204.8 | 18330134.4 | 30446102.4 | 48449673.6 | 74555798.4 | 111305990.4 | 161610921.6 | 228267676.8 | 228267676.8 | 228267676.8 | 228267676.8 | 228267676.8 | 228267676.8
Costs |  | 16706649.5848 | 0 | 0 | 11253388.3553 | 173020.846 | 177346.3671 | 181780.0263 | 186324.5269 | 190982.6401 | 195757.2061 | 200651.1363 | 205667.4147 | 210809.1001 | 216079.3276 | 221481.3107 | 12908973.2632
Net Economic Benefit |  | 966579395.0065
Option 1b
Weighted EUSE (MVAh) |  |  | 70.6 | 127.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Cost of EUSE |  | 8996204.701 | 3341049.3 | 6015388.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Benefits |  | 983286044.5913 | 0 | 0 | 10606204.8 | 18330134.4 | 30446102.4 | 48449673.6 | 74555798.4 | 111305990.4 | 161610921.6 | 228267676.8 | 228267676.8 | 228267676.8 | 228267676.8 | 228267676.8 | 228267676.8
Costs |  | 12600280.8428 | 0 | 0 | 7187159.4161 | 110502.576 | 113265.1404 | 116096.7689 | 118999.1882 | 121974.1679 | 125023.5221 | 128149.1101 | 131352.8379 | 134636.6588 | 138002.5753 | 141452.6397 | 12826943.8754
Net Economic Benefit |  | 970685763.7485
Option 1c
Weighted EUSE (MVAh) |  |  | 70.6 | 127.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Cost of EUSE |  | 8996204.701 | 3341049.3 | 6015388.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Benefits |  | 983286044.5913 | 0 | 0 | 10606204.8 | 18330134.4 | 30446102.4 | 48449673.6 | 74555798.4 | 111305990.4 | 161610921.6 | 228267676.8 | 228267676.8 | 228267676.8 | 228267676.8 | 228267676.8 | 228267676.8
Costs |  | 16947354.7441 | 0 | 0 | 9457500.6658 | 145409.0727 | 149044.2996 | 2666937.4082 | 195244.9849 | 200126.1095 | 205129.2622 | 210257.4938 | 215513.9311 | 220901.7794 | 226424.3239 | 232084.932 | 12919841.975
Net Economic Benefit |  | 966338689.8471
Option 1d
Weighted EUSE (MVAh) |  |  | 70.6 | 127.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Cost of EUSE |  | 8996204.701 | 3341049.3 | 6015388.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Benefits |  | 983286044.5913 | 0 | 0 | 10606204.8 | 18330134.4 | 30446102.4 | 48449673.6 | 74555798.4 | 111305990.4 | 161610921.6 | 228267676.8 | 228267676.8 | 228267676.8 | 228267676.8 | 228267676.8 | 228267676.8
Costs |  | 12905270.7377 | 0 | 0 | 5454928.0782 | 83869.5192 | 85966.2572 | 2602282.4148 | 128973.6166 | 132197.957 | 135502.9059 | 138890.4786 | 142362.7405 | 145921.8091 | 149569.8543 | 153309.1006 | 12839096.7479
Net Economic Benefit |  | 970380773.8536
Option 2
Weighted EUSE (MVAh) |  |  | 70.6 | 127.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Cost of EUSE |  | 8996204.701 | 3341049.3 | 6015388.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Benefits |  | 983286044.5913 | 0 | 0 | 10606204.8 | 18330134.4 | 30446102.4 | 48449673.6 | 74555798.4 | 111305990.4 | 161610921.6 | 228267676.8 | 228267676.8 | 228267676.8 | 228267676.8 | 228267676.8 | 228267676.8
Costs |  | 19727480.3167 | 0 | 0 | 17500404.0111 | 269068.7117 | 275795.4295 | 2796857.3164 | 328412.8907 | 336623.213 | 345038.7933 | 353664.7631 | 362506.3822 | 371569.0418 | 380858.2678 | 390379.7245 | 400139.2176
Net Economic Benefit |  | 963558564.2746
Option 3
Weighted EUSE (MVAh) |  |  | 70.6 | 127.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Cost of EUSE |  | 8996204.701 | 3341049.3 | 6015388.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Benefits |  | 983286044.5913 | 0 | 0 | 10606204.8 | 18330134.4 | 30446102.4 | 48449673.6 | 74555798.4 | 111305990.4 | 161610921.6 | 228267676.8 | 228267676.8 | 228267676.8 | 228267676.8 | 228267676.8 | 228267676.8
Costs |  | 45588156.8546 | 0 | 0 | 45142532.0842 | 694066.4308 | 711418.0916 | 729203.5439 | 747433.6324 | 766119.4733 | 785272.4601 | 804904.2716 | 825026.8784 | 845652.5503 | 866793.8641 | 888463.7107 | 910675.3035
Net Economic Benefit |  | 937697887.7367
Option 4
Weighted EUSE (MVAh) |  |  | 70.6 | 127.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Cost of EUSE |  | 9000308.9267 | 3341049.3 | 6015388.8 | 0 | 0 | 143.256 | 312.996 | 317.244 | 458.784 | 795.564 | 930.696 | 930.696 | 930.696 | 930.696 | 930.696 | 930.696
Benefits |  | 983281940.3656 | 0 | 0 | 10606204.8 | 18330134.4 | 30445959.144 | 48449360.604 | 74555481.156 | 111305531.616 | 161610126.036 | 228266746.104 | 228266746.104 | 228266746.104 | 228266746.104 | 228266746.104 | 228266746.104
Costs |  | 16484495.381 | 0 | 0 | 6964925.8054 | 107085.7343 | 109762.8776 | 5140840.952 | 192630.2586 | 197446.015 | 202382.1654 | 207441.7196 | 212627.7625 | 217943.4566 | 223392.043 | 228976.8441 | 12916656.1849
Net Economic Benefit |  | 966797444.9846
Option 5a
Weighted EUSE (MVAh) |  |  | 70.6 | 127.1 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Cost of EUSE |  | 9021302.2369 | 3341049.3 | 6015388.8 | 28396.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Benefits |  | 983260947.0554 | 0 | 0 | 10577808 | 18330134.4 | 30446102.4 | 48449673.6 | 74555798.4 | 111305990.4 | 161610921.6 | 228267676.8 | 228267676.8 | 228267676.8 | 228267676.8 | 228267676.8 | 228267676.8
Costs |  | 13855050.8228 | 0 | 0 | 1785090.625 | 7366838.4015 | 113265.1404 | 116096.7689 | 118999.1882 | 121974.1679 | 125023.5221 | 128149.1101 | 131352.8379 | 134636.6588 | 138002.5753 | 141452.6397 | 12826943.8754
Net Economic Benefit |  | 969405896.2326
Option 5b
Weighted EUSE (MVAh) |  |  | 70.6 | 70.4 | 124.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Cost of EUSE |  | 12978458.2313 | 3341049.3 | 4729637.724 | 5873404.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Benefits |  | 979303791.0609 | 0 | 1285751.076 | 4732800 | 18330134.4 | 30446102.4 | 48449673.6 | 74555798.4 | 111305990.4 | 161610921.6 | 228267676.8 | 228267676.8 | 228267676.8 | 228267676.8 | 228267676.8 | 228267676.8
Costs |  | 19009411.1462 | 0 | 0 | 7617031.25 | 7366838.4015 | 113265.1404 | 116096.7689 | 118999.1882 | 121974.1679 | 125023.5221 | 128149.1101 | 131352.8379 | 134636.6588 | 138002.5753 | 141452.6397 | 12826943.8754
Net Economic Benefit |  | 960294379.9147
Option 6
Weighted EUSE (MVAh) |  |  | 70.6 | 127.1 | 223.9 | 386.9 | 642.6 | 1022.6 | 1573.6 | 2349.2 | 3410.8 | 4817.4 | 4817.4 | 4817.4 | 4817.4 | 4817.4 | 4817.4
Weighted Cost of EUSE |  | 229067580.8874 | 3341049.3 | 4729637.724 | 7050638.988 | 10178685.972 | 16194211.344 | 20314614.948 | 20931889.608 | 26784815.256 | 34744173.984 | 42480385.92 | 42480385.92 | 42480385.92 | 42480385.92 | 42480385.92 | 42480385.92
Benefits |  | 763214668.4049 | 0 | 1285751.076 | 3555565.812 | 8151448.428 | 14251891.056 | 28135058.652 | 53623908.792 | 84521175.144 | 126866747.616 | 185787290.88 | 185787290.88 | 185787290.88 | 185787290.88 | 185787290.88 | 185787290.88
Costs |  | 12803193.8748 | 0 | 0 | 1285369.1118 | 19762.5501 | 20256.6138 | 7563264.0328 | 137248.0579 | 140679.2593 | 144196.2408 | 147801.1468 | 151496.1755 | 155283.5799 | 159165.6694 | 163144.8111 | 12849178.3511
Net Economic Benefit |  | 750411474.5301
Option 7
Weighted EUSE (MVAh) |  |  | 70.6 | 127.1 | 223.9 | 386.9 | 642.6 | 1022.6 | 1573.6 | 2349.2 | 3410.8 | 4817.4 | 4817.4 | 4817.4 | 4817.4 | 4817.4 | 4817.4
Weighted Cost of EUSE |  | 229067580.8874 | 3341049.3 | 4729637.724 | 7050638.988 | 10178685.972 | 16194211.344 | 20314614.948 | 20931889.608 | 26784815.256 | 34744173.984 | 42480385.92 | 42480385.92 | 42480385.92 | 42480385.92 | 42480385.92 | 42480385.92
Benefits |  | 763214668.4049 | 0 | 1285751.076 | 3555565.812 | 8151448.428 | 14251891.056 | 28135058.652 | 53623908.792 | 84521175.144 | 126866747.616 | 185787290.88 | 185787290.88 | 185787290.88 | 185787290.88 | 185787290.88 | 185787290.88
Costs |  | 13158122.7172 | 0 | 0 | 1636828.5206 | 25166.2385 | 25795.3945 | 7568941.2829 | 143067.2392 | 146643.9202 | 150310.0182 | 154067.7687 | 157919.4629 | 161867.4495 | 165914.1357 | 170061.9891 | 12856268.4585
Net Economic Benefit |  | 750056545.6876

## Cost-Benefit (VCR-20%)
VCR | 31552 |  | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Discount Rate | 6.37%
Option costs ($2016 Real)
Do Nothing
Weighted EUSE (MVAh) |  |  | 70.6 | 127.1 | 224.1 | 387.3 | 643.3 | 1023.7 | 1575.3 | 2351.8 | 3414.7 | 4823.1 | 4823.1 | 4823.1 | 4823.1 | 4823.1 | 4823.1
Weighted Cost of EUSE |  | 661521499.5282 | 2227366.2 | 4010259.2 | 7070803.2 | 12220089.6 | 20297401.6 | 32299782.4 | 49703865.6 | 74203993.6 | 107740614.4 | 152178451.2 | 152178451.2 | 152178451.2 | 152178451.2 | 152178451.2 | 152178451.2
Benefits |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Costs |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Net Economic Benefit |  | 0
Option 1a
Weighted EUSE (MVAh) |  |  | 70.6 | 127.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Cost of EUSE |  | 5997469.8006 | 2227366.2 | 4010259.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Benefits |  | 655524029.7275 | 0 | 0 | 7070803.2 | 12220089.6 | 20297401.6 | 32299782.4 | 49703865.6 | 74203993.6 | 107740614.4 | 152178451.2 | 152178451.2 | 152178451.2 | 152178451.2 | 152178451.2 | 152178451.2
Costs |  | 16706649.5848 | 0 | 0 | 11253388.3553 | 173020.846 | 177346.3671 | 181780.0263 | 186324.5269 | 190982.6401 | 195757.2061 | 200651.1363 | 205667.4147 | 210809.1001 | 216079.3276 | 221481.3107 | 12908973.2632
Net Economic Benefit |  | 638817380.1427
Option 1b
Weighted EUSE (MVAh) |  |  | 70.6 | 127.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Cost of EUSE |  | 5997469.8006 | 2227366.2 | 4010259.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Benefits |  | 655524029.7275 | 0 | 0 | 7070803.2 | 12220089.6 | 20297401.6 | 32299782.4 | 49703865.6 | 74203993.6 | 107740614.4 | 152178451.2 | 152178451.2 | 152178451.2 | 152178451.2 | 152178451.2 | 152178451.2
Costs |  | 12600280.8428 | 0 | 0 | 7187159.4161 | 110502.576 | 113265.1404 | 116096.7689 | 118999.1882 | 121974.1679 | 125023.5221 | 128149.1101 | 131352.8379 | 134636.6588 | 138002.5753 | 141452.6397 | 12826943.8754
Net Economic Benefit |  | 642923748.8847
Option 1c
Weighted EUSE (MVAh) |  |  | 70.6 | 127.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Cost of EUSE |  | 5997469.8006 | 2227366.2 | 4010259.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Benefits |  | 655524029.7275 | 0 | 0 | 7070803.2 | 12220089.6 | 20297401.6 | 32299782.4 | 49703865.6 | 74203993.6 | 107740614.4 | 152178451.2 | 152178451.2 | 152178451.2 | 152178451.2 | 152178451.2 | 152178451.2
Costs |  | 16947354.7441 | 0 | 0 | 9457500.6658 | 145409.0727 | 149044.2996 | 2666937.4082 | 195244.9849 | 200126.1095 | 205129.2622 | 210257.4938 | 215513.9311 | 220901.7794 | 226424.3239 | 232084.932 | 12919841.975
Net Economic Benefit |  | 638576674.9834
Option 1d
Weighted EUSE (MVAh) |  |  | 70.6 | 127.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Cost of EUSE |  | 5997469.8006 | 2227366.2 | 4010259.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Benefits |  | 655524029.7275 | 0 | 0 | 7070803.2 | 12220089.6 | 20297401.6 | 32299782.4 | 49703865.6 | 74203993.6 | 107740614.4 | 152178451.2 | 152178451.2 | 152178451.2 | 152178451.2 | 152178451.2 | 152178451.2
Costs |  | 12905270.7377 | 0 | 0 | 5454928.0782 | 83869.5192 | 85966.2572 | 2602282.4148 | 128973.6166 | 132197.957 | 135502.9059 | 138890.4786 | 142362.7405 | 145921.8091 | 149569.8543 | 153309.1006 | 12839096.7479
Net Economic Benefit |  | 642618758.9898
Option 2
Weighted EUSE (MVAh) |  |  | 70.6 | 127.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Cost of EUSE |  | 5997469.8006 | 2227366.2 | 4010259.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Benefits |  | 655524029.7275 | 0 | 0 | 7070803.2 | 12220089.6 | 20297401.6 | 32299782.4 | 49703865.6 | 74203993.6 | 107740614.4 | 152178451.2 | 152178451.2 | 152178451.2 | 152178451.2 | 152178451.2 | 152178451.2
Costs |  | 19727480.3167 | 0 | 0 | 17500404.0111 | 269068.7117 | 275795.4295 | 2796857.3164 | 328412.8907 | 336623.213 | 345038.7933 | 353664.7631 | 362506.3822 | 371569.0418 | 380858.2678 | 390379.7245 | 400139.2176
Net Economic Benefit |  | 635796549.4109
Option 3
Weighted EUSE (MVAh) |  |  | 70.6 | 127.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Cost of EUSE |  | 5997469.8006 | 2227366.2 | 4010259.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Benefits |  | 655524029.7275 | 0 | 0 | 7070803.2 | 12220089.6 | 20297401.6 | 32299782.4 | 49703865.6 | 74203993.6 | 107740614.4 | 152178451.2 | 152178451.2 | 152178451.2 | 152178451.2 | 152178451.2 | 152178451.2
Costs |  | 45588156.8546 | 0 | 0 | 45142532.0842 | 694066.4308 | 711418.0916 | 729203.5439 | 747433.6324 | 766119.4733 | 785272.4601 | 804904.2716 | 825026.8784 | 845652.5503 | 866793.8641 | 888463.7107 | 910675.3035
Net Economic Benefit |  | 609935872.873
Option 4
Weighted EUSE (MVAh) |  |  | 70.6 | 127.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Cost of EUSE |  | 6000205.9511 | 2227366.2 | 4010259.2 | 0 | 0 | 95.504 | 208.664 | 211.496 | 305.856 | 530.376 | 620.464 | 620.464 | 620.464 | 620.464 | 620.464 | 620.464
Benefits |  | 655521293.5771 | 0 | 0 | 7070803.2 | 12220089.6 | 20297306.096 | 32299573.736 | 49703654.104 | 74203687.744 | 107740084.024 | 152177830.736 | 152177830.736 | 152177830.736 | 152177830.736 | 152177830.736 | 152177830.736
Costs |  | 16484495.381 | 0 | 0 | 6964925.8054 | 107085.7343 | 109762.8776 | 5140840.952 | 192630.2586 | 197446.015 | 202382.1654 | 207441.7196 | 212627.7625 | 217943.4566 | 223392.043 | 228976.8441 | 12916656.1849
Net Economic Benefit |  | 639036798.1961
Option 5a
Weighted EUSE (MVAh) |  |  | 70.6 | 127.1 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Cost of EUSE |  | 6014201.4912 | 2227366.2 | 4010259.2 | 18931.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Benefits |  | 655507298.0369 | 0 | 0 | 7051872 | 12220089.6 | 20297401.6 | 32299782.4 | 49703865.6 | 74203993.6 | 107740614.4 | 152178451.2 | 152178451.2 | 152178451.2 | 152178451.2 | 152178451.2 | 152178451.2
Costs |  | 13855050.8228 | 0 | 0 | 1785090.625 | 7366838.4015 | 113265.1404 | 116096.7689 | 118999.1882 | 121974.1679 | 125023.5221 | 128149.1101 | 131352.8379 | 134636.6588 | 138002.5753 | 141452.6397 | 12826943.8754
Net Economic Benefit |  | 641652247.2142
Option 5b
Weighted EUSE (MVAh) |  |  | 70.6 | 70.4 | 124.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Cost of EUSE |  | 8652305.4875 | 2227366.2 | 3153091.816 | 3915603.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Benefits |  | 652869194.0406 | 0 | 857167.384 | 3155200 | 12220089.6 | 20297401.6 | 32299782.4 | 49703865.6 | 74203993.6 | 107740614.4 | 152178451.2 | 152178451.2 | 152178451.2 | 152178451.2 | 152178451.2 | 152178451.2
Costs |  | 19009411.1462 | 0 | 0 | 7617031.25 | 7366838.4015 | 113265.1404 | 116096.7689 | 118999.1882 | 121974.1679 | 125023.5221 | 128149.1101 | 131352.8379 | 134636.6588 | 138002.5753 | 141452.6397 | 12826943.8754
Net Economic Benefit |  | 633859782.8944
Option 6
Weighted EUSE (MVAh) |  |  | 70.6 | 127.1 | 223.9 | 386.9 | 642.6 | 1022.6 | 1573.6 | 2349.2 | 3410.8 | 4817.4 | 4817.4 | 4817.4 | 4817.4 | 4817.4 | 4817.4
Weighted Cost of EUSE |  | 152711720.5916 | 2227366.2 | 3153091.816 | 4700425.992 | 6785790.648 | 10796140.896 | 13543076.632 | 13954593.072 | 17856543.504 | 23162782.656 | 28320257.28 | 28320257.28 | 28320257.28 | 28320257.28 | 28320257.28 | 28320257.28
Benefits |  | 508809778.9366 | 0 | 857167.384 | 2370377.208 | 5434298.952 | 9501260.704 | 18756705.768 | 35749272.528 | 56347450.096 | 84577831.744 | 123858193.92 | 123858193.92 | 123858193.92 | 123858193.92 | 123858193.92 | 123858193.92
Costs |  | 12803193.8748 | 0 | 0 | 1285369.1118 | 19762.5501 | 20256.6138 | 7563264.0328 | 137248.0579 | 140679.2593 | 144196.2408 | 147801.1468 | 151496.1755 | 155283.5799 | 159165.6694 | 163144.8111 | 12849178.3511
Net Economic Benefit |  | 496006585.0618
Option 7
Weighted EUSE (MVAh) |  |  | 70.6 | 127.1 | 223.9 | 386.9 | 642.6 | 1022.6 | 1573.6 | 2349.2 | 3410.8 | 4817.4 | 4817.4 | 4817.4 | 4817.4 | 4817.4 | 4817.4
Weighted Cost of EUSE |  | 152711720.5916 | 2227366.2 | 3153091.816 | 4700425.992 | 6785790.648 | 10796140.896 | 13543076.632 | 13954593.072 | 17856543.504 | 23162782.656 | 28320257.28 | 28320257.28 | 28320257.28 | 28320257.28 | 28320257.28 | 28320257.28
Benefits |  | 508809778.9366 | 0 | 857167.384 | 2370377.208 | 5434298.952 | 9501260.704 | 18756705.768 | 35749272.528 | 56347450.096 | 84577831.744 | 123858193.92 | 123858193.92 | 123858193.92 | 123858193.92 | 123858193.92 | 123858193.92
Costs |  | 13158122.7172 | 0 | 0 | 1636828.5206 | 25166.2385 | 25795.3945 | 7568941.2829 | 143067.2392 | 146643.9202 | 150310.0182 | 154067.7687 | 157919.4629 | 161867.4495 | 165914.1357 | 170061.9891 | 12856268.4585
Net Economic Benefit |  | 495651656.2194

## Cost-Benefit (Disc rate high)
VCR | 39440 |  | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Discount Rate | 8.26% | Option costs ($2016 Real)
2016-2030
Do Nothing
Weighted EUSE (MVAh) |  |  | 70.6 | 127.1 | 224.1 | 387.3 | 643.3 | 1023.7 | 1575.3 | 2351.8 | 3414.7 | 4823.1 | 4823.1 | 4823.1 | 4823.1 | 4823.1 | 4823.1
Weighted Cost of EUSE |  | 698195438.0895 | 2784207.75 | 5012824 | 8838504 | 15275112 | 25371752 | 40374728 | 62129832 | 92754992 | 134675768 | 190223064 | 190223064 | 190223064 | 190223064 | 190223064 | 190223064
Benefits |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Costs |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Net Economic Benefit |  | 0
Option 1a
Weighted EUSE (MVAh) |  |  | 70.6 | 127.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Cost of EUSE |  | 7414564.299 | 2784207.75 | 5012824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Benefits |  | 690780873.7904 | 0 | 0 | 8838504 | 15275112 | 25371752 | 40374728 | 62129832 | 92754992 | 134675768 | 190223064 | 190223064 | 190223064 | 190223064 | 190223064 | 190223064
Costs |  | 15009539.6522 | 0 | 0 | 11253388.3553 | 173020.846 | 177346.3671 | 181780.0263 | 186324.5269 | 190982.6401 | 195757.2061 | 200651.1363 | 205667.4147 | 210809.1001 | 216079.3276 | 221481.3107 | 12908973.2632
Net Economic Benefit |  | 675771334.1382
Option 1b
Weighted EUSE (MVAh) |  |  | 70.6 | 127.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Cost of EUSE |  | 7414564.299 | 2784207.75 | 5012824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Benefits |  | 690780873.7904 | 0 | 0 | 8838504 | 15275112 | 25371752 | 40374728 | 62129832 | 92754992 | 134675768 | 190223064 | 190223064 | 190223064 | 190223064 | 190223064 | 190223064
Costs |  | 11094576.4046 | 0 | 0 | 7187159.4161 | 110502.576 | 113265.1404 | 116096.7689 | 118999.1882 | 121974.1679 | 125023.5221 | 128149.1101 | 131352.8379 | 134636.6588 | 138002.5753 | 141452.6397 | 12826943.8754
Net Economic Benefit |  | 679686297.3858
Option 1c
Weighted EUSE (MVAh) |  |  | 70.6 | 127.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Cost of EUSE |  | 7414564.299 | 2784207.75 | 5012824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Benefits |  | 690780873.7904 | 0 | 0 | 8838504 | 15275112 | 25371752 | 40374728 | 62129832 | 92754992 | 134675768 | 190223064 | 190223064 | 190223064 | 190223064 | 190223064 | 190223064
Costs |  | 15146493.1743 | 0 | 0 | 9457500.6658 | 145409.0727 | 149044.2996 | 2666937.4082 | 195244.9849 | 200126.1095 | 205129.2622 | 210257.4938 | 215513.9311 | 220901.7794 | 226424.3239 | 232084.932 | 12919841.975
Net Economic Benefit |  | 675634380.6161
Option 1d
Weighted EUSE (MVAh) |  |  | 70.6 | 127.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Cost of EUSE |  | 7414564.299 | 2784207.75 | 5012824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Benefits |  | 690780873.7904 | 0 | 0 | 8838504 | 15275112 | 25371752 | 40374728 | 62129832 | 92754992 | 134675768 | 190223064 | 190223064 | 190223064 | 190223064 | 190223064 | 190223064
Costs |  | 11292818.2309 | 0 | 0 | 5454928.0782 | 83869.5192 | 85966.2572 | 2602282.4148 | 128973.6166 | 132197.957 | 135502.9059 | 138890.4786 | 142362.7405 | 145921.8091 | 149569.8543 | 153309.1006 | 12839096.7479
Net Economic Benefit |  | 679488055.5595
Option 2
Weighted EUSE (MVAh) |  |  | 70.6 | 127.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Cost of EUSE |  | 7414564.299 | 2784207.75 | 5012824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Benefits |  | 690780873.7904 | 0 | 0 | 8838504 | 15275112 | 25371752 | 40374728 | 62129832 | 92754992 | 134675768 | 190223064 | 190223064 | 190223064 | 190223064 | 190223064 | 190223064
Costs |  | 18715413.7992 | 0 | 0 | 17500404.0111 | 269068.7117 | 275795.4295 | 2796857.3164 | 328412.8907 | 336623.213 | 345038.7933 | 353664.7631 | 362506.3822 | 371569.0418 | 380858.2678 | 390379.7245 | 400139.2176
Net Economic Benefit |  | 672065459.9912
Option 3
Weighted EUSE (MVAh) |  |  | 70.6 | 127.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Cost of EUSE |  | 7414564.299 | 2784207.75 | 5012824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Benefits |  | 690780873.7904 | 0 | 0 | 8838504 | 15275112 | 25371752 | 40374728 | 62129832 | 92754992 | 134675768 | 190223064 | 190223064 | 190223064 | 190223064 | 190223064 | 190223064
Costs |  | 43463207.965 | 0 | 0 | 45142532.0842 | 694066.4308 | 711418.0916 | 729203.5439 | 747433.6324 | 766119.4733 | 785272.4601 | 804904.2716 | 825026.8784 | 845652.5503 | 866793.8641 | 888463.7107 | 910675.3035
Net Economic Benefit |  | 647317665.8254
Option 4
Weighted EUSE (MVAh) |  |  | 70.6 | 127.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Cost of EUSE |  | 7417446.8143 | 2784207.75 | 5012824 | 0 | 0 | 119.38 | 260.83 | 264.37 | 382.32 | 662.97 | 775.58 | 775.58 | 775.58 | 775.58 | 775.58 | 775.58
Benefits |  | 690777991.2751 | 0 | 0 | 8838504 | 15275112 | 25371632.62 | 40374467.17 | 62129567.63 | 92754609.68 | 134675105.03 | 190222288.42 | 190222288.42 | 190222288.42 | 190222288.42 | 190222288.42 | 190222288.42
Costs |  | 14612676.6265 | 0 | 0 | 6964925.8054 | 107085.7343 | 109762.8776 | 5140840.952 | 192630.2586 | 197446.015 | 202382.1654 | 207441.7196 | 212627.7625 | 217943.4566 | 223392.043 | 228976.8441 | 12916656.1849
Net Economic Benefit |  | 676165314.6486
Option 5a
Weighted EUSE (MVAh) |  |  | 70.6 | 127.1 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Cost of EUSE |  | 7434755.0332 | 2784207.75 | 5012824 | 23664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Benefits |  | 690760683.0562 | 0 | 0 | 8814840 | 15275112 | 25371752 | 40374728 | 62129832 | 92754992 | 134675768 | 190223064 | 190223064 | 190223064 | 190223064 | 190223064 | 190223064
Costs |  | 12204302.7748 | 0 | 0 | 1785090.625 | 7366838.4015 | 113265.1404 | 116096.7689 | 118999.1882 | 121974.1679 | 125023.5221 | 128149.1101 | 131352.8379 | 134636.6588 | 138002.5753 | 141452.6397 | 12826943.8754
Net Economic Benefit |  | 678556380.2814
Option 5b
Weighted EUSE (MVAh) |  |  | 70.6 | 70.4 | 124.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Cost of EUSE |  | 10600971.9057 | 2784207.75 | 3941364.77 | 4894504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Benefits |  | 687594466.1838 | 0 | 1071459.23 | 3944000 | 15275112 | 25371752 | 40374728 | 62129832 | 92754992 | 134675768 | 190223064 | 190223064 | 190223064 | 190223064 | 190223064 | 190223064
Costs |  | 17180264.6964 | 0 | 0 | 7617031.25 | 7366838.4015 | 113265.1404 | 116096.7689 | 118999.1882 | 121974.1679 | 125023.5221 | 128149.1101 | 131352.8379 | 134636.6588 | 138002.5753 | 141452.6397 | 12826943.8754
Net Economic Benefit |  | 670414201.4874
Option 6
Weighted EUSE (MVAh) |  |  | 70.6 | 127.1 | 223.9 | 386.9 | 642.6 | 1022.6 | 1573.6 | 2349.2 | 3410.8 | 4817.4 | 4817.4 | 4817.4 | 4817.4 | 4817.4 | 4817.4
Weighted Cost of EUSE |  | 164368592.0153 | 2784207.75 | 3941364.77 | 5875532.49 | 8482238.31 | 13495176.12 | 16928845.79 | 17443241.34 | 22320679.38 | 28953478.32 | 35400321.6 | 35400321.6 | 35400321.6 | 35400321.6 | 35400321.6 | 35400321.6
Benefits |  | 533826846.0742 | 0 | 1071459.23 | 2962971.51 | 6792873.69 | 11876575.88 | 23445882.21 | 44686590.66 | 70434312.62 | 105722289.68 | 154822742.4 | 154822742.4 | 154822742.4 | 154822742.4 | 154822742.4 | 154822742.4
Costs |  | 11010435.5176 | 0 | 0 | 1285369.1118 | 19762.5501 | 20256.6138 | 7563264.0328 | 137248.0579 | 140679.2593 | 144196.2408 | 147801.1468 | 151496.1755 | 155283.5799 | 159165.6694 | 163144.8111 | 12849178.3511
Net Economic Benefit |  | 522816410.5566
Option 7
Weighted EUSE (MVAh) |  |  | 70.6 | 127.1 | 223.9 | 386.9 | 642.6 | 1022.6 | 1573.6 | 2349.2 | 3410.8 | 4817.4 | 4817.4 | 4817.4 | 4817.4 | 4817.4 | 4817.4
Weighted Cost of EUSE |  | 164368592.0153 | 2784207.75 | 3941364.77 | 5875532.49 | 8482238.31 | 13495176.12 | 16928845.79 | 17443241.34 | 22320679.38 | 28953478.32 | 35400321.6 | 35400321.6 | 35400321.6 | 35400321.6 | 35400321.6 | 35400321.6
Benefits |  | 533826846.0742 | 0 | 1071459.23 | 2962971.51 | 6792873.69 | 11876575.88 | 23445882.21 | 44686590.66 | 70434312.62 | 105722289.68 | 154822742.4 | 154822742.4 | 154822742.4 | 154822742.4 | 154822742.4 | 154822742.4
Costs |  | 11348820.4657 | 0 | 0 | 1636828.5206 | 25166.2385 | 25795.3945 | 7568941.2829 | 143067.2392 | 146643.9202 | 150310.0182 | 154067.7687 | 157919.4629 | 161867.4495 | 165914.1357 | 170061.9891 | 12856268.4585
Net Economic Benefit |  | 522478025.6085

## Cost-Benefit (Cost+30%)
VCR | 39440 |  | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Discount Rate | 6.37% | Option costs ($2016 Real)
Project Cost Sensitivity | 1.3 | 2016-2030
Do Nothing
Weighted EUSE (MVAh) |  |  | 70.6 | 127.1 | 224.1 | 387.3 | 643.3 | 1023.7 | 1575.3 | 2351.8 | 3414.7 | 4823.1 | 4823.1 | 4823.1 | 4823.1 | 4823.1 | 4823.1
Weighted Cost of EUSE |  | 826901874.4102 | 2784207.75 | 5012824 | 8838504 | 15275112 | 25371752 | 40374728 | 62129832 | 92754992 | 134675768 | 190223064 | 190223064 | 190223064 | 190223064 | 190223064 | 190223064
Benefits |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Costs |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Net Economic Benefit |  | 0
Option 1a
Weighted EUSE (MVAh) |  |  | 70.6 | 127.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Cost of EUSE |  | 7496837.2508 | 2784207.75 | 5012824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Benefits |  | 819405037.1594 | 0 | 0 | 8838504 | 15275112 | 25371752 | 40374728 | 62129832 | 92754992 | 134675768 | 190223064 | 190223064 | 190223064 | 190223064 | 190223064 | 190223064
Costs |  | 21718644.4602 | 0 | 0 | 14629404.8619 | 224927.0998 | 230550.2772 | 236314.0342 | 242221.885 | 248277.4322 | 254484.368 | 260846.4772 | 267367.6391 | 274051.8301 | 280903.1258 | 287925.704 | 16781665.2422
Net Economic Benefit |  | 797686392.6992
Option 1b
Weighted EUSE (MVAh) |  |  | 70.6 | 127.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Cost of EUSE |  | 7496837.2508 | 2784207.75 | 5012824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Benefits |  | 819405037.1594 | 0 | 0 | 8838504 | 15275112 | 25371752 | 40374728 | 62129832 | 92754992 | 134675768 | 190223064 | 190223064 | 190223064 | 190223064 | 190223064 | 190223064
Costs |  | 16380365.0957 | 0 | 0 | 9343307.241 | 143653.3488 | 147244.6826 | 150925.7996 | 154698.9446 | 158566.4182 | 162530.5787 | 166593.8431 | 170758.6892 | 175027.6565 | 179403.3479 | 183888.4316 | 16675027.038
Net Economic Benefit |  | 803024672.0637
Option 1c
Weighted EUSE (MVAh) |  |  | 70.6 | 127.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Cost of EUSE |  | 7496837.2508 | 2784207.75 | 5012824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Benefits |  | 819405037.1594 | 0 | 0 | 8838504 | 15275112 | 25371752 | 40374728 | 62129832 | 92754992 | 134675768 | 190223064 | 190223064 | 190223064 | 190223064 | 190223064 | 190223064
Costs |  | 22031561.1674 | 0 | 0 | 12294750.8656 | 189031.7946 | 193757.5894 | 3467018.6307 | 253818.4803 | 260163.9423 | 266668.0409 | 273334.7419 | 280168.1105 | 287172.3132 | 294351.6211 | 301710.4116 | 16795794.5675
Net Economic Benefit |  | 797373475.992
Option 1d
Weighted EUSE (MVAh) |  |  | 70.6 | 127.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Cost of EUSE |  | 7496837.2508 | 2784207.75 | 5012824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Benefits |  | 819405037.1594 | 0 | 0 | 8838504 | 15275112 | 25371752 | 40374728 | 62129832 | 92754992 | 134675768 | 190223064 | 190223064 | 190223064 | 190223064 | 190223064 | 190223064
Costs |  | 16776851.959 | 0 | 0 | 7091406.5016 | 109030.375 | 111756.1343 | 3382967.1393 | 167665.7016 | 171857.3441 | 176153.7777 | 180557.6222 | 185071.5627 | 189698.3518 | 194440.8106 | 199301.8308 | 16690825.7722
Net Economic Benefit |  | 802628185.2004
Option 2
Weighted EUSE (MVAh) |  |  | 70.6 | 127.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Cost of EUSE |  | 7496837.2508 | 2784207.75 | 5012824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Benefits |  | 819405037.1594 | 0 | 0 | 8838504 | 15275112 | 25371752 | 40374728 | 62129832 | 92754992 | 134675768 | 190223064 | 190223064 | 190223064 | 190223064 | 190223064 | 190223064
Costs |  | 25645724.4117 | 0 | 0 | 22750525.2145 | 349789.3252 | 358534.0583 | 3635914.5113 | 426936.7579 | 437610.1769 | 448550.4313 | 459764.1921 | 471258.2969 | 483039.7543 | 495115.7482 | 507493.6419 | 520180.9829
Net Economic Benefit |  | 793759312.7477
Option 3
Weighted EUSE (MVAh) |  |  | 70.6 | 127.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Cost of EUSE |  | 7496837.2508 | 2784207.75 | 5012824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Benefits |  | 819405037.1594 | 0 | 0 | 8838504 | 15275112 | 25371752 | 40374728 | 62129832 | 92754992 | 134675768 | 190223064 | 190223064 | 190223064 | 190223064 | 190223064 | 190223064
Costs |  | 59264603.9109 | 0 | 0 | 58685291.7094 | 902286.36 | 924843.519 | 947964.607 | 971663.7222 | 995955.3152 | 1020854.1981 | 1046375.5531 | 1072534.9419 | 1099348.3154 | 1126832.0233 | 1155002.8239 | 1183877.8945
Net Economic Benefit |  | 760140433.2485
Option 4
Weighted EUSE (MVAh) |  |  | 70.6 | 127.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Cost of EUSE |  | 7500257.4389 | 2784207.75 | 5012824 | 0 | 0 | 119.38 | 260.83 | 264.37 | 382.32 | 662.97 | 775.58 | 775.58 | 775.58 | 775.58 | 775.58 | 775.58
Benefits |  | 819401616.9713 | 0 | 0 | 8838504 | 15275112 | 25371632.62 | 40374467.17 | 62129567.63 | 92754609.68 | 134675105.03 | 190222288.42 | 190222288.42 | 190222288.42 | 190222288.42 | 190222288.42 | 190222288.42
Costs |  | 21429843.9953 | 0 | 0 | 9054403.547 | 139211.4545 | 142691.7409 | 6683093.2375 | 250419.3362 | 256679.8196 | 263096.815 | 269674.2354 | 276416.0913 | 283326.4936 | 290409.6559 | 297669.8973 | 16791653.0404
Net Economic Benefit |  | 797971772.976
Option 5a
Weighted EUSE (MVAh) |  |  | 70.6 | 127.1 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Cost of EUSE |  | 7517751.8641 | 2784207.75 | 5012824 | 23664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Benefits |  | 819384122.5462 | 0 | 0 | 8814840 | 15275112 | 25371752 | 40374728 | 62129832 | 92754992 | 134675768 | 190223064 | 190223064 | 190223064 | 190223064 | 190223064 | 190223064
Costs |  | 18011566.0696 | 0 | 0 | 2320617.8125 | 9576889.922 | 147244.6826 | 150925.7996 | 154698.9446 | 158566.4182 | 162530.5787 | 166593.8431 | 170758.6892 | 175027.6565 | 179403.3479 | 183888.4316 | 16675027.038
Net Economic Benefit |  | 801372556.4766
Option 5b
Weighted EUSE (MVAh) |  |  | 70.6 | 70.4 | 124.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Cost of EUSE |  | 10815381.8594 | 2784207.75 | 3941364.77 | 4894504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Benefits |  | 816086492.5508 | 0 | 1071459.23 | 3944000 | 15275112 | 25371752 | 40374728 | 62129832 | 92754992 | 134675768 | 190223064 | 190223064 | 190223064 | 190223064 | 190223064 | 190223064
Costs |  | 24712234.4901 | 0 | 0 | 9902140.625 | 9576889.922 | 147244.6826 | 150925.7996 | 154698.9446 | 158566.4182 | 162530.5787 | 166593.8431 | 170758.6892 | 175027.6565 | 179403.3479 | 183888.4316 | 16675027.038
Net Economic Benefit |  | 791374258.0607
Option 6
Weighted EUSE (MVAh) |  |  | 70.6 | 127.1 | 223.9 | 386.9 | 642.6 | 1022.6 | 1573.6 | 2349.2 | 3410.8 | 4817.4 | 4817.4 | 4817.4 | 4817.4 | 4817.4 | 4817.4
Weighted Cost of EUSE |  | 190889650.7395 | 2784207.75 | 3941364.77 | 5875532.49 | 8482238.31 | 13495176.12 | 16928845.79 | 17443241.34 | 22320679.38 | 28953478.32 | 35400321.6 | 35400321.6 | 35400321.6 | 35400321.6 | 35400321.6 | 35400321.6
Benefits |  | 636012223.6707 | 0 | 1071459.23 | 2962971.51 | 6792873.69 | 11876575.88 | 23445882.21 | 44686590.66 | 70434312.62 | 105722289.68 | 154822742.4 | 154822742.4 | 154822742.4 | 154822742.4 | 154822742.4 | 154822742.4
Costs |  | 16644152.0372 | 0 | 0 | 1670979.8453 | 25691.3151 | 26333.598 | 9832243.2426 | 178422.4752 | 182883.0371 | 187455.113 | 192141.4908 | 196945.0281 | 201868.6538 | 206915.3702 | 212088.2544 | 16703931.8564
Net Economic Benefit |  | 619368071.6335
Option 7
Weighted EUSE (MVAh) |  |  | 70.6 | 127.1 | 223.9 | 386.9 | 642.6 | 1022.6 | 1573.6 | 2349.2 | 3410.8 | 4817.4 | 4817.4 | 4817.4 | 4817.4 | 4817.4 | 4817.4
Weighted Cost of EUSE |  | 190889650.7395 | 2784207.75 | 3941364.77 | 5875532.49 | 8482238.31 | 13495176.12 | 16928845.79 | 17443241.34 | 22320679.38 | 28953478.32 | 35400321.6 | 35400321.6 | 35400321.6 | 35400321.6 | 35400321.6 | 35400321.6
Benefits |  | 636012223.6707 | 0 | 1071459.23 | 2962971.51 | 6792873.69 | 11876575.88 | 23445882.21 | 44686590.66 | 70434312.62 | 105722289.68 | 154822742.4 | 154822742.4 | 154822742.4 | 154822742.4 | 154822742.4 | 154822742.4
Costs |  | 17105559.5324 | 0 | 0 | 2127877.0768 | 32716.1101 | 33534.0128 | 9839623.6678 | 185987.411 | 190637.0963 | 195403.0237 | 200288.0993 | 205295.3018 | 210427.6843 | 215688.3764 | 221080.5858 | 16713148.9961
Net Economic Benefit |  | 618906664.1383

## Cost-Benefit (Cost-30%)
VCR | 39440 |  | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Discount Rate | 6.37% | Option costs ($2016 Real)
Project Cost Sensitivity | 0.7 | 2016-2030
Do Nothing
Weighted EUSE (MVAh) |  |  | 70.6 | 127.1 | 224.1 | 387.3 | 643.3 | 1023.7 | 1575.3 | 2351.8 | 3414.7 | 4823.1 | 4823.1 | 4823.1 | 4823.1 | 4823.1 | 4823.1
Weighted Cost of EUSE |  | 826901874.4102 | 2784207.75 | 5012824 | 8838504 | 15275112 | 25371752 | 40374728 | 62129832 | 92754992 | 134675768 | 190223064 | 190223064 | 190223064 | 190223064 | 190223064 | 190223064
Benefits |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Costs |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Net Economic Benefit |  | 0
Option 1a
Weighted EUSE (MVAh) |  |  | 70.6 | 127.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Cost of EUSE |  | 7496837.2508 | 2784207.75 | 5012824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Benefits |  | 819405037.1594 | 0 | 0 | 8838504 | 15275112 | 25371752 | 40374728 | 62129832 | 92754992 | 134675768 | 190223064 | 190223064 | 190223064 | 190223064 | 190223064 | 190223064
Costs |  | 11694654.7094 | 0 | 0 | 7877371.8487 | 121114.5922 | 124142.457 | 127246.0184 | 130427.1689 | 133687.8481 | 137030.0443 | 140455.7954 | 143967.1903 | 147566.37 | 151255.5293 | 155036.9175 | 9036281.2843
Net Economic Benefit |  | 807710382.45
Option 1b
Weighted EUSE (MVAh) |  |  | 70.6 | 127.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Cost of EUSE |  | 7496837.2508 | 2784207.75 | 5012824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Benefits |  | 819405037.1594 | 0 | 0 | 8838504 | 15275112 | 25371752 | 40374728 | 62129832 | 92754992 | 134675768 | 190223064 | 190223064 | 190223064 | 190223064 | 190223064 | 190223064
Costs |  | 8820196.59 | 0 | 0 | 5031011.5913 | 77351.8032 | 79285.5983 | 81267.7383 | 83299.4317 | 85381.9175 | 87516.4654 | 89704.3771 | 91946.9865 | 94245.6612 | 96601.8027 | 99016.8478 | 8978860.7128
Net Economic Benefit |  | 810584840.5694
Option 1c
Weighted EUSE (MVAh) |  |  | 70.6 | 127.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Cost of EUSE |  | 7496837.2508 | 2784207.75 | 5012824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Benefits |  | 819405037.1594 | 0 | 0 | 8838504 | 15275112 | 25371752 | 40374728 | 62129832 | 92754992 | 134675768 | 190223064 | 190223064 | 190223064 | 190223064 | 190223064 | 190223064
Costs |  | 11863148.3209 | 0 | 0 | 6620250.4661 | 101786.3509 | 104331.0097 | 1866856.1858 | 136671.4894 | 140088.2766 | 143590.4836 | 147180.2456 | 150859.7518 | 154631.2456 | 158497.0267 | 162459.4524 | 9043889.3825
Net Economic Benefit |  | 807541888.8385
Option 1d
Weighted EUSE (MVAh) |  |  | 70.6 | 127.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Cost of EUSE |  | 6489542.6847 | 2784207.75 | 3941364.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Benefits |  | 820412331.7256 | 0 | 1071459.23 | 8838504 | 15275112 | 25371752 | 40374728 | 62129832 | 92754992 | 134675768 | 190223064 | 190223064 | 190223064 | 190223064 | 190223064 | 190223064
Costs |  | 9033689.5164 | 0 | 0 | 3818449.6547 | 58708.6634 | 60176.38 | 1821597.6904 | 90281.5316 | 92538.5699 | 94852.0342 | 97223.335 | 99653.9184 | 102145.2663 | 104698.898 | 107316.3705 | 8987367.7235
Net Economic Benefit |  | 811378642.2092
Option 2
Weighted EUSE (MVAh) |  |  | 70.6 | 127.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Cost of EUSE |  | 7496837.2508 | 2784207.75 | 5012824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Benefits |  | 819405037.1594 | 0 | 0 | 8838504 | 15275112 | 25371752 | 40374728 | 62129832 | 92754992 | 134675768 | 190223064 | 190223064 | 190223064 | 190223064 | 190223064 | 190223064
Costs |  | 13809236.2217 | 0 | 0 | 12250282.8078 | 188348.0982 | 193056.8006 | 1957800.1215 | 229889.0235 | 235636.2491 | 241527.1553 | 247565.3342 | 253754.4676 | 260098.3292 | 266600.7875 | 273265.8072 | 280097.4523
Net Economic Benefit |  | 805595800.9377
Option 3
Weighted EUSE (MVAh) |  |  | 70.6 | 127.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Cost of EUSE |  | 7496837.2508 | 2784207.75 | 5012824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Benefits |  | 819405037.1594 | 0 | 0 | 8838504 | 15275112 | 25371752 | 40374728 | 62129832 | 92754992 | 134675768 | 190223064 | 190223064 | 190223064 | 190223064 | 190223064 | 190223064
Costs |  | 31911709.7982 | 0 | 0 | 31599772.4589 | 485846.5016 | 497992.6641 | 510442.4807 | 523203.5427 | 536283.6313 | 549690.7221 | 563432.9901 | 577518.8149 | 591956.7852 | 606755.7049 | 621924.5975 | 637472.7124
Net Economic Benefit |  | 787493327.3612
Option 4
Weighted EUSE (MVAh) |  |  | 70.6 | 127.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Cost of EUSE |  | 7500257.4389 | 2784207.75 | 5012824 | 0 | 0 | 119.38 | 260.83 | 264.37 | 382.32 | 662.97 | 775.58 | 775.58 | 775.58 | 775.58 | 775.58 | 775.58
Benefits |  | 819401616.9713 | 0 | 0 | 8838504 | 15275112 | 25371632.62 | 40374467.17 | 62129567.63 | 92754609.68 | 134675105.03 | 190222288.42 | 190222288.42 | 190222288.42 | 190222288.42 | 190222288.42 | 190222288.42
Costs |  | 11539146.7667 | 0 | 0 | 4875448.0638 | 74960.014 | 76834.0143 | 3598588.6664 | 134841.181 | 138212.2105 | 141667.5158 | 145209.2037 | 148839.4338 | 152560.4196 | 156374.4301 | 160283.7909 | 9041659.3294
Net Economic Benefit |  | 807862470.2046
Option 5a
Weighted EUSE (MVAh) |  |  | 70.6 | 127.1 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Cost of EUSE |  | 7517751.8641 | 2784207.75 | 5012824 | 23664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Benefits |  | 819384122.5462 | 0 | 0 | 8814840 | 15275112 | 25371752 | 40374728 | 62129832 | 92754992 | 134675768 | 190223064 | 190223064 | 190223064 | 190223064 | 190223064 | 190223064
Costs |  | 9698535.5759 | 0 | 0 | 1249563.4375 | 5156786.8811 | 79285.5983 | 81267.7383 | 83299.4317 | 85381.9175 | 87516.4654 | 89704.3771 | 91946.9865 | 94245.6612 | 96601.8027 | 99016.8478 | 8978860.7128
Net Economic Benefit |  | 809685586.9702
Option 5b
Weighted EUSE (MVAh) |  |  | 70.6 | 70.4 | 124.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Cost of EUSE |  | 10815381.8594 | 2784207.75 | 3941364.77 | 4894504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Benefits |  | 816086492.5508 | 0 | 1071459.23 | 3944000 | 15275112 | 25371752 | 40374728 | 62129832 | 92754992 | 134675768 | 190223064 | 190223064 | 190223064 | 190223064 | 190223064 | 190223064
Costs |  | 13306587.8023 | 0 | 0 | 5331921.875 | 5156786.8811 | 79285.5983 | 81267.7383 | 83299.4317 | 85381.9175 | 87516.4654 | 89704.3771 | 91946.9865 | 94245.6612 | 96601.8027 | 99016.8478 | 8978860.7128
Net Economic Benefit |  | 802779904.7484
Option 6
Weighted EUSE (MVAh) |  |  | 70.6 | 127.1 | 223.9 | 386.9 | 642.6 | 1022.6 | 1573.6 | 2349.2 | 3410.8 | 4817.4 | 4817.4 | 4817.4 | 4817.4 | 4817.4 | 4817.4
Weighted Cost of EUSE |  | 190889650.7395 | 2784207.75 | 3941364.77 | 5875532.49 | 8482238.31 | 13495176.12 | 16928845.79 | 17443241.34 | 22320679.38 | 28953478.32 | 35400321.6 | 35400321.6 | 35400321.6 | 35400321.6 | 35400321.6 | 35400321.6
Benefits |  | 636012223.6707 | 0 | 1071459.23 | 2962971.51 | 6792873.69 | 11876575.88 | 23445882.21 | 44686590.66 | 70434312.62 | 105722289.68 | 154822742.4 | 154822742.4 | 154822742.4 | 154822742.4 | 154822742.4 | 154822742.4
Costs |  | 8962235.7123 | 0 | 0 | 899758.3782 | 13833.7851 | 14179.6297 | 5294284.823 | 96073.6405 | 98475.4815 | 100937.3685 | 103460.8028 | 106047.3228 | 108698.5059 | 111415.9685 | 114201.3678 | 8994424.8458
Net Economic Benefit |  | 627049987.9584
Option 7
Weighted EUSE (MVAh) |  |  | 70.6 | 127.1 | 223.9 | 386.9 | 642.6 | 1022.6 | 1573.6 | 2349.2 | 3410.8 | 4817.4 | 4817.4 | 4817.4 | 4817.4 | 4817.4 | 4817.4
Weighted Cost of EUSE |  | 190889650.7395 | 2784207.75 | 3941364.77 | 5875532.49 | 8482238.31 | 13495176.12 | 16928845.79 | 17443241.34 | 22320679.38 | 28953478.32 | 35400321.6 | 35400321.6 | 35400321.6 | 35400321.6 | 35400321.6 | 35400321.6
Benefits |  | 636012223.6707 | 0 | 1071459.23 | 2962971.51 | 6792873.69 | 11876575.88 | 23445882.21 | 44686590.66 | 70434312.62 | 105722289.68 | 154822742.4 | 154822742.4 | 154822742.4 | 154822742.4 | 154822742.4 | 154822742.4
Costs |  | 9210685.9021 | 0 | 0 | 1145779.9644 | 17616.367 | 18056.7761 | 5298258.898 | 100147.0675 | 102650.7442 | 105217.0128 | 107847.4381 | 110543.624 | 113307.2146 | 116139.895 | 119043.3924 | 8999387.921
Net Economic Benefit |  | 626801537.7687