## Report summary Table
Table 8-2: Market benefits of augmentation options relative to the base case
Augmentation option | Total lifecycle project cost (2017-2032) ($M, real 2017) | NPV of net economic benefit (2017-2032 ) $M | Project ranking
Base Case - Do Nothing |  |  | N/A
Option 1 - Reconductor the 66kV loop with higher capacity conductor in 2019 | 13.084 | 322.2096 | 2
Option 2 - Install a new KTS-MAT 66kV line to form a four legged 66kV loop in 2019 | 15.376 | 321.3372 | 3
Option 3 - Split the existing 66kV loop by installing one additional 66kV line in 2019 | 5.646 | 282.7687 | 4
Option 4 - Split the existing 66kV loop by installing two additional 66kV lines in 2019 | 10.431 | 326.6215 | 1

## Sensitivity Analysis Summary
Option | Net Economic Benefit ($) | Rank | Net Economic Benefit ($) | Rank | Net Economic Benefit ($) | Rank | Net Economic Benefit ($) | Rank | Net Economic Benefit ($) | Rank | Net Economic Benefit ($) | Rank | Average Net Economic benefit ($) | Overall Rank of Feasible Options | Include Option in Ranking?
| Base (planning) scenario |  | VCR High (+20%) |  | VCR Low (-20%) |  | Discount Rate High (8.26%) |  | Investment Cost High (+30%) |  | Investment Cost Low (-30%)
Option 1 | 322209585.922 | 2 | 392350001.9408 | 2 | 256901788.0639 | 2 | 272814065.2922 | 2 | 320427503.0954 | 2 | 328824286.9093 | 2 | 315587871.8706 | 2 | yes
Option 2 | 321337246.7113 | 3 | 391793499.5367 | 3 | 255713612.0466 | 3 | 271780670.9884 | 3 | 318819706.9115 | 3 | 328687404.6717 | 3 | 314688690.1444 | 3 | yes
Option 3 | 282768671.9734 | 4 | 343429769.0054 | 4 | 226940193.1021 | 4 | 240426633.7875 | 4 | 283373293.4424 | 4 | 286996668.6651 | 4 | 277322538.3293 | 4 | yes
Option 4 | 326621468.8803 | 1 | 397076732.0029 | 1 | 260998823.9184 | 1 | 276811257.7538 | 1 | 325690680.2855 | 1 | 332384875.6358 | 1 | 319930639.7461 | 1 | yes

## Opt 3 - Economic timing
Discount Rate | 6.37%
PV cost (Capital and Operational) $ | 6038958.7044
Year | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
Base case ( Do nothing) EUSE | 300245.2746 | 2414580.5918 | 10509330.9846 | 21635078.3283 | 26086640.486 | 33786780.4013 | 38633973.8088 | 52442966.1779 | 63956927.6781 | 63956927.6781 | 63956927.6781 | 63956927.6781 | 63956927.6781 | 63956927.6781 | 63956927.6781
Annualised benefits after implementation of Option 3 ($) | -300245.2746 | -2414580.5918 | 10509330.9846 | 21635078.3283 | 26086640.486 | 33786780.4013 | 38633973.8088 | 52442966.1779 | 63956927.6781 | 63956927.6781 | 63956927.6781 | 63956927.6781 | 63956927.6781 | 63956927.6781 | 63956927.6781
Annualised benefits after implementation of Option 3 ($M) | -0.30025 | -2.4146 | 10.5093 | 21.6351 | 26.0866 | 33.7868 | 38.634 | 52.443 | 63.9569 | 63.9569 | 63.9569 | 63.9569 | 63.9569 | 63.9569 | 63.9569
Annualised cost for Option 3 ($) | 403064.6864 | 403064.6864 | 403064.6864 | 403064.6864 | 403064.6864 | 403064.6864 | 403064.6864 | 403064.6864 | 403064.6864 | 403064.6864 | 403064.6864 | 403064.6864 | 403064.6864 | 403064.6864 | 403064.6864
Annualised cost for Option 3 ($M) | 0.40306 | 0.40306 | 0.40306 | 0.40306 | 0.40306 | 0.40306 | 0.40306 | 0.40306 | 0.40306 | 0.40306 | 0.40306 | 0.40306 | 0.40306 | 0.40306 | 0.40306

## Option Costs
Year |  | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
Discount Rate | 6.37%
Inflation Rate | 2.5%
O&M cost | 1.5%
Option 1 |  | 0 | 13746377.5 | 211350.5541 | 216634.3179 | 222050.1759 | 227601.4303 | 233291.466 | 239123.7527 | 245101.8465 | 251229.3926 | 257510.1275 | 263947.8806 | 270546.5777 | 277310.2421 | 284242.9982
Capital |  | 0 | 13746377.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Operational |  | 0 | 0 | 211350.5541 | 216634.3179 | 222050.1759 | 227601.4303 | 233291.466 | 239123.7527 | 245101.8465 | 251229.3926 | 257510.1275 | 263947.8806 | 270546.5777 | 277310.2421 | 284242.9982
Option 2 |  | 0 | 16154410 | 248374.0537 | 254583.4051 | 260947.9902 | 267471.69 | 274158.4822 | 281012.4443 | 288037.7554 | 295238.6993 | 302619.6668 | 310185.1584 | 317939.7874 | 325889.2821 | 334037.5045
Capital |  | 0 | 16154410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2
Operational |  | 0 | 0 | 248374.0537 | 254583.4051 | 260947.9902 | 267471.69 | 274158.4822 | 281012.4443 | 288037.7554 | 295238.6993 | 302619.6668 | 310185.1584 | 317939.7874 | 325888.2821 | 334035.5045
Option 3 |  | 0 | 5931828.75 | 91201.867 | 93481.9137 | 95818.9615 | 98214.4356 | 100669.7965 | 103186.5414 | 105766.2049 | 108410.36 | 111120.619 | 113898.6345 | 116746.1004 | 119664.7529 | 122656.3717
Capital |  | 0 | 5931828.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Operational |  | 0 | 0 | 91201.867 | 93481.9137 | 95818.9615 | 98214.4356 | 100669.7965 | 103186.5414 | 105766.2049 | 108410.36 | 111120.619 | 113898.6345 | 116746.1004 | 119664.7529 | 122656.3717
Option 4 |  | 0 | 10959069.375 | 168495.6916 | 172708.0839 | 177025.786 | 181451.4307 | 185987.7164 | 190637.4094 | 195403.3446 | 200288.4282 | 205295.6389 | 210428.0299 | 215688.7306 | 221080.9489 | 226607.9726
Capital |  | 0 | 10959069.375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Operational |  | 0 | 0 | 168495.6916 | 172708.0839 | 177025.786 | 181451.4307 | 185987.7164 | 190637.4094 | 195403.3446 | 200288.4282 | 205295.6389 | 210428.0299 | 215688.7306 | 221080.9489 | 226607.9726
| Real $2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
Option 1 - Reconductor the 66kV loop with higher capacity conductor in 2019 | 13084000 | 13411100 | 13746377.5 | 14090036.9375 | 14442287.8609 | 14803345.0575 | 15173428.6839 | 15552764.401 | 15941583.511 | 16340123.0988 | 16748626.1763 | 17167341.8307 | 17596525.3764 | 18036438.5108 | 18487349.4736 | 18949533.2105
Option 2 - Install a new KTS-MAT 66kV line to form a four legged 66kV loop in 2019 | 15376000 | 15760400 | 16154410 | 16558270.25 | 16972227.0062 | 17396532.6814 | 17831445.9984 | 18277232.1484 | 18734162.9521 | 19202517.0259 | 19682579.9516 | 20174644.4504 | 20679010.5616 | 21195985.8257 | 21725885.4713 | 22269032.6081
Option 3 - Split the existing 66kV loop by installing one additional 66kV line in 2019 | 5646000 | 5787150 | 5931828.75 | 6080124.4687 | 6232127.5805 | 6387930.77 | 6547629.0392 | 6711319.7652 | 6879102.7593 | 7051080.3283 | 7227357.3365 | 7408041.2699 | 7593242.3017 | 7783073.3592 | 7977650.1932 | 8177091.448
Option 4 - Split the existing 66kV loop by installing two additional 66kV lines in 2019 | 10431000 | 10691775 | 10959069.375 | 11233046.1094 | 11513872.2621 | 11801719.0687 | 12096762.0454 | 12399181.0965 | 12709160.6239 | 13026889.6395 | 13352561.8805 | 13686375.9275 | 14028535.3257 | 14379248.7089 | 14738729.9266 | 15107198.1747

## Cost-Benefit (BASE)
VCR | 39440 |  | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
Discount Rate | 6.37%
Option costs | $2017 Real
Do Nothing
Weighted EUSE (MWh) |  |  | 7.6127 | 61.2216 | 266.4638 | 548.5568 | 661.426 | 856.6628 | 979.5632 | 1329.6898 | 1621.626 | 1621.626 | 1621.626 | 1621.626 | 1621.626 | 1621.626 | 1621.626
Weighted Cost of EUSE |  |  | 300245.2746 | 2414580.5918 | 10509330.9846 | 21635078.3283 | 26086640.486 | 33786780.4013 | 38633973.8088 | 52442966.1779 | 63956927.6781 | 63956927.6781 | 63956927.6781 | 63956927.6781 | 63956927.6781 | 63956927.6781 | 63956927.6781
Benefits |  | -342616072.8865 | -300245.2746 | -2414580.5918 | -10509330.9846 | -21635078.3283 | -26086640.486 | -33786780.4013 | -38633973.8088 | -52442966.1779 | -63956927.6781 | -63956927.6781 | -63956927.6781 | -63956927.6781 | -63956927.6781 | -63956927.6781 | -63956927.6781
Costs |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Net Economic Benefit |  | -342616072.8865
Option 1
Weighted EUSE (MWh) |  |  | 7.6127 | 61.2216 | 0.010864 | 0.031786 | 0.044041 | 0.85907 | 2.3245 | 6.7994 | 10.0316 | 10.0316 | 10.0316 | 10.0316 | 10.0316 | 10.0316 | 10.0316
Weighted Cost of EUSE |  | 3995538.1943 | 300245.2746 | 2414580.5918 | 428.4832 | 1253.6266 | 1736.9939 | 33881.6291 | 91676.9799 | 268167.1858 | 395648.0728 | 395648.0728 | 395648.0728 | 395648.0728 | 395648.0728 | 395648.0728 | 395648.0728
Benefits |  | 336204225.6118 | -300245.2746 | -2414580.5918 | 10508902.5014 | 21633824.7017 | 26084903.4921 | 33752898.7722 | 38542296.8289 | 52174798.9922 | 63561279.6053 | 63561279.6053 | 63561279.6053 | 63561279.6053 | 63561279.6053 | 63561279.6053 | 63561279.6053
Costs |  | 13994639.6898 | 0 | 13746377.5 | 211350.5541 | 216634.3179 | 222050.1759 | 227601.4303 | 233291.466 | 239123.7527 | 245101.8465 | 251229.3926 | 257510.1275 | 263947.8806 | 270546.5777 | 277310.2421 | 284242.9982
Net Economic Benefit |  | 322209585.922
Option 2
Weighted EUSE (MWh) |  |  | 7.6127 | 61.2216 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 0.00034
Weighted Cost of EUSE |  | 2416354.1611 | 300245.2746 | 2414580.5918 | 0 | 0 | 0 | 0 | 0 | 0 | 13.4096 | 13.4096 | 13.4096 | 13.4096 | 13.4096 | 13.4096 | 13.4096
Benefits |  | 337783409.645 | -300245.2746 | -2414580.5918 | 10509330.9846 | 21635078.3283 | 26086640.486 | 33786780.4013 | 38633973.8088 | 52442966.1779 | 63956914.2685 | 63956914.2685 | 63956914.2685 | 63956914.2685 | 63956914.2685 | 63956914.2685 | 63956914.2685
Costs |  | 16446162.9337 | 0 | 16154410 | 248374.0537 | 254583.4051 | 260947.9902 | 267471.69 | 274158.4822 | 281012.4443 | 288037.7554 | 295238.6993 | 302619.6668 | 310185.1584 | 317939.7874 | 325889.2821 | 334037.5045
Net Economic Benefit |  | 321337246.7113
Option 3
Weighted EUSE (MWh) |  |  | 7.6127 | 61.2216 | 55.8482 | 44.4638 | 69.4326 | 107.3405 | 135.3571 | 231.7711 | 239.8346 | 239.8346 | 239.8346 | 239.8346 | 239.8346 | 239.8346 | 239.8346
Weighted Cost of EUSE |  | 51392133.1283 | 300245.2746 | 2414580.5918 | 2202653.6663 | 1753653.0303 | 2738419.8656 | 4233509.1849 | 5338485.6937 | 9141050.4345 | 9459077.8359 | 9459077.8359 | 9459077.8359 | 9459077.8359 | 9459077.8359 | 9459077.8359 | 9459077.8359
Benefits |  | 288807630.6778 | -300245.2746 | -2414580.5918 | 8306677.3184 | 19881425.298 | 23348220.6204 | 29553271.2164 | 33295488.1151 | 43301915.7434 | 54497849.8423 | 54497849.8423 | 54497849.8423 | 54497849.8423 | 54497849.8423 | 54497849.8423 | 54497849.8423
Costs |  | 6038958.7044 | 0 | 5931828.75 | 91201.867 | 93481.9137 | 95818.9615 | 98214.4356 | 100669.7965 | 103186.5414 | 105766.2049 | 108410.36 | 111120.619 | 113898.6345 | 116746.1004 | 119664.7529 | 122656.3717
Net Economic Benefit |  | 282768671.9734
Option 4
Weighted EUSE (MWh) |  |  | 7.6127 | 61.2216 | 0 | 0.0068524 | 0.0095512 | 0.0091869 | 0.012882 | 0.020969 | 0.025804 | 0.025804 | 0.025804 | 0.025804 | 0.025804 | 0.025804 | 0.025804
Weighted Cost of EUSE |  | 2421302.6754 | 300245.2746 | 2414580.5918 | 0 | 270.2599 | 376.7003 | 362.3314 | 508.0724 | 827.0111 | 1017.7041 | 1017.7041 | 1017.7041 | 1017.7041 | 1017.7041 | 1017.7041 | 1017.7041
Benefits |  | 337778461.1307 | -300245.2746 | -2414580.5918 | 10509330.9846 | 21634808.0684 | 26086263.7857 | 33786418.0699 | 38633465.7364 | 52442139.1668 | 63955909.974 | 63955909.974 | 63955909.974 | 63955909.974 | 63955909.974 | 63955909.974 | 63955909.974
Costs |  | 11156992.2504 | 0 | 10959069.375 | 168495.6916 | 172708.0839 | 177025.786 | 181451.4307 | 185987.7164 | 190637.4094 | 195403.3446 | 200288.4282 | 205295.6389 | 210428.0299 | 215688.7306 | 221080.9489 | 226607.9726
Net Economic Benefit |  | 326621468.8803
Note: Option 4 addresses KTS-TMA-MAT EUSE but AW-PV becomes two legged loop making things worse during KTS-AW outage. Hence the NPV is -ve for this option
|  |  | 7.6127 | 61.2216 | 55.8482 | 44.4638 | 69.4326 | 107.3405 | 135.3571 | 231.7711 | 239.8346 | 239.8346 | 239.8346 | 239.8346 | 239.8346 | 239.8346 | 239.8346

## Cost-Benefit (VCR+20%)
VCR | 47328 |  | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
Discount Rate | 6.37%
Option costs | $2017 Real
Do Nothing
Weighted EUSE (MWh) |  |  | 7.6127 | 61.2216 | 266.4638 | 548.5568 | 661.426 | 856.6628 | 979.5632 | 1329.6898 | 1621.626 | 1621.626 | 1621.626 | 1621.626 | 1621.626 | 1621.626 | 1621.626
Weighted Cost of EUSE |  | 411139287.4638 | 360294.3295 | 2897496.7101 | 12611197.1816 | 25962093.9939 | 31303968.5832 | 40544136.4816 | 46360768.5706 | 62931559.4135 | 76748313.2138 | 76748313.2138 | 76748313.2138 | 76748313.2138 | 76748313.2138 | 76748313.2138 | 76748313.2138
Benefits |  | -411139287.4638 | -360294.3295 | -2897496.7101 | -12611197.1816 | -25962093.9939 | -31303968.5832 | -40544136.4816 | -46360768.5706 | -62931559.4135 | -76748313.2138 | -76748313.2138 | -76748313.2138 | -76748313.2138 | -76748313.2138 | -76748313.2138 | -76748313.2138
Costs |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Net Economic Benefit |  | -411139287.4638
Option 1
Weighted EUSE (MWh) |  |  | 7.6127 | 61.2216 | 0.010864 | 0.031786 | 0.044041 | 0.85907 | 2.3245 | 6.7994 | 10.0316 | 10.0316 | 10.0316 | 10.0316 | 10.0316 | 10.0316 | 10.0316
Weighted Cost of EUSE |  | 4794645.8332 | 360294.3295 | 2897496.7101 | 514.1798 | 1504.352 | 2084.3927 | 40657.955 | 110012.3758 | 321800.6229 | 474777.6874 | 474777.6874 | 474777.6874 | 474777.6874 | 474777.6874 | 474777.6874 | 474777.6874
Benefits |  | 406344641.6306 | 0 | 0 | 12610683.0017 | 25960589.642 | 31301884.1905 | 40503478.5266 | 46250756.1947 | 62609758.7906 | 76273535.5264 | 76273535.5264 | 76273535.5264 | 76273535.5264 | 76273535.5264 | 76273535.5264 | 76273535.5264
Costs |  | 13994639.6898 | 0 | 13746377.5 | 211350.5541 | 216634.3179 | 222050.1759 | 227601.4303 | 233291.466 | 239123.7527 | 245101.8465 | 251229.3926 | 257510.1275 | 263947.8806 | 270546.5777 | 277310.2421 | 284242.9982
Net Economic Benefit |  | 392350001.9408
Option 2
Weighted EUSE (MWh) |  |  | 7.6127 | 61.2216 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 0.00034
Weighted Cost of EUSE |  | 2899624.9933 | 360294.3295 | 2897496.7101 | 0 | 0 | 0 | 0 | 0 | 0 | 16.0915 | 16.0915 | 16.0915 | 16.0915 | 16.0915 | 16.0915 | 16.0915
Benefits |  | 408239662.4704 | 0 | 0 | 12611197.1816 | 25962093.9939 | 31303968.5832 | 40544136.4816 | 46360768.5706 | 62931559.4135 | 76748297.1222 | 76748297.1222 | 76748297.1222 | 76748297.1222 | 76748297.1222 | 76748297.1222 | 76748297.1222
Costs |  | 16446162.9337 | 0 | 16154410 | 248374.0537 | 254583.4051 | 260947.9902 | 267471.69 | 274158.4822 | 281012.4443 | 288037.7554 | 295238.6993 | 302619.6668 | 310185.1584 | 317939.7874 | 325889.2821 | 334037.5045
Net Economic Benefit |  | 391793499.5367
Option 3
Weighted EUSE (MWh) |  |  | 7.6127 | 61.2216 | 55.8482 | 44.4638 | 69.4326 | 107.3405 | 135.3571 | 231.7711 | 239.8346 | 239.8346 | 239.8346 | 239.8346 | 239.8346 | 239.8346 | 239.8346
Weighted Cost of EUSE |  | 61670559.754 | 360294.3295 | 2897496.7101 | 2643184.3995 | 2104383.6363 | 3286103.8387 | 5080211.0219 | 6406182.8324 | 10969260.5214 | 11350893.403 | 11350893.403 | 11350893.403 | 11350893.403 | 11350893.403 | 11350893.403 | 11350893.403
Benefits |  | 349468727.7098 | 0 | 0 | 9968012.7821 | 23857710.3576 | 28017864.7445 | 35463925.4597 | 39954585.7382 | 51962298.8921 | 65397419.8107 | 65397419.8107 | 65397419.8107 | 65397419.8107 | 65397419.8107 | 65397419.8107 | 65397419.8107
Costs |  | 6038958.7044 | 0 | 5931828.75 | 91201.867 | 93481.9137 | 95818.9615 | 98214.4356 | 100669.7965 | 103186.5414 | 105766.2049 | 108410.36 | 111120.619 | 113898.6345 | 116746.1004 | 119664.7529 | 122656.3717
Net Economic Benefit |  | 343429769.0054
Option 4
Weighted EUSE (MWh) |  |  | 7.6127 | 61.2216 | 0 | 0.0068524 | 0.0095512 | 0.0091869 | 0.012882 | 0.020969 | 0.025804 | 0.025804 | 0.025804 | 0.025804 | 0.025804 | 0.025804 | 0.025804
Weighted Cost of EUSE |  | 2905563.2105 | 360294.3295 | 2897496.7101 | 0 | 324.3119 | 452.0404 | 434.7977 | 609.6869 | 992.4133 | 1221.2449 | 1221.2449 | 1221.2449 | 1221.2449 | 1221.2449 | 1221.2449 | 1221.2449
Benefits |  | 408233724.2533 | 0 | 0 | 12611197.1816 | 25961769.682 | 31303516.5428 | 40543701.6839 | 46360158.8837 | 62930567.0002 | 76747091.9688 | 76747091.9688 | 76747091.9688 | 76747091.9688 | 76747091.9688 | 76747091.9688 | 76747091.9688
Costs |  | 11156992.2504 | 0 | 10959069.375 | 168495.6916 | 172708.0839 | 177025.786 | 181451.4307 | 185987.7164 | 190637.4094 | 195403.3446 | 200288.4282 | 205295.6389 | 210428.0299 | 215688.7306 | 221080.9489 | 226607.9726
Net Economic Benefit |  | 397076732.0029

## Cost-Benefit (VCR-20%)
VCR | 31552 |  | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
Discount Rate | 6.37%
Option costs | $2017 Real
Do Nothing
Weighted EUSE (MWh) |  |  | 7.6127 | 61.2216 | 266.4638 | 548.5568 | 661.426 | 856.6628 | 979.5632 | 1329.6898 | 1621.626 | 1621.626 | 1621.626 | 1621.626 | 1621.626 | 1621.626 | 1621.626
Weighted Cost of EUSE |  | 274092858.3092 | 240196.2197 | 1931664.4734 | 8407464.7877 | 17308062.6626 | 20869312.3888 | 27029424.3211 | 30907179.047 | 41954372.9423 | 51165542.1425 | 51165542.1425 | 51165542.1425 | 51165542.1425 | 51165542.1425 | 51165542.1425 | 51165542.1425
Benefits |  | -274092858.3092 | -240196.2197 | -1931664.4734 | -8407464.7877 | -17308062.6626 | -20869312.3888 | -27029424.3211 | -30907179.047 | -41954372.9423 | -51165542.1425 | -51165542.1425 | -51165542.1425 | -51165542.1425 | -51165542.1425 | -51165542.1425 | -51165542.1425
Costs |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Net Economic Benefit |  | -274092858.3092
Option 1
Weighted EUSE (MWh) |  |  | 7.6127 | 61.2216 | 0.010864 | 0.031786 | 0.044041 | 0.85907 | 2.3245 | 6.7994 | 10.0316 | 10.0316 | 10.0316 | 10.0316 | 10.0316 | 10.0316 | 10.0316
Weighted Cost of EUSE |  | 3196430.5554 | 240196.2197 | 1931664.4734 | 342.7866 | 1002.9013 | 1389.5951 | 27105.3033 | 73341.5839 | 214533.7486 | 316518.4583 | 316518.4583 | 316518.4583 | 316518.4583 | 316518.4583 | 316518.4583 | 316518.4583
Benefits |  | 270896427.7538 | 0 | 0 | 8407122.0011 | 17307059.7613 | 20867922.7937 | 27002319.0178 | 30833837.4632 | 41739839.1937 | 50849023.6842 | 50849023.6842 | 50849023.6842 | 50849023.6842 | 50849023.6842 | 50849023.6842 | 50849023.6842
Costs |  | 13994639.6898 | 0 | 13746377.5 | 211350.5541 | 216634.3179 | 222050.1759 | 227601.4303 | 233291.466 | 239123.7527 | 245101.8465 | 251229.3926 | 257510.1275 | 263947.8806 | 270546.5777 | 277310.2421 | 284242.9982
Net Economic Benefit |  | 256901788.0639
Option 2
Weighted EUSE (MWh) |  |  | 7.6127 | 61.2216 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 0.00034
Weighted Cost of EUSE |  | 1933083.3289 | 240196.2197 | 1931664.4734 | 0 | 0 | 0 | 0 | 0 | 0 | 10.7277 | 10.7277 | 10.7277 | 10.7277 | 10.7277 | 10.7277 | 10.7277
Benefits |  | 272159774.9803 | 0 | 0 | 8407464.7877 | 17308062.6626 | 20869312.3888 | 27029424.3211 | 30907179.047 | 41954372.9423 | 51165531.4148 | 51165531.4148 | 51165531.4148 | 51165531.4148 | 51165531.4148 | 51165531.4148 | 51165531.4148
Costs |  | 16446162.9337 | 0 | 16154410 | 248374.0537 | 254583.4051 | 260947.9902 | 267471.69 | 274158.4822 | 281012.4443 | 288037.7554 | 295238.6993 | 302619.6668 | 310185.1584 | 317939.7874 | 325889.2821 | 334037.5045
Net Economic Benefit |  | 255713612.0466
Option 3
Weighted EUSE (MWh) |  |  | 7.6127 | 61.2216 | 55.8482 | 44.4638 | 69.4326 | 107.3405 | 135.3571 | 231.7711 | 239.8346 | 239.8346 | 239.8346 | 239.8346 | 239.8346 | 239.8346 | 239.8346
Weighted Cost of EUSE |  | 41113706.5026 | 240196.2197 | 1931664.4734 | 1762122.933 | 1402922.4242 | 2190735.8925 | 3386807.3479 | 4270788.5549 | 7312840.3476 | 7567262.2687 | 7567262.2687 | 7567262.2687 | 7567262.2687 | 7567262.2687 | 7567262.2687 | 7567262.2687
Benefits |  | 232979151.8065 | 0 | 0 | 6645341.8547 | 15905140.2384 | 18678576.4963 | 23642616.9731 | 26636390.4921 | 34641532.5947 | 43598279.8738 | 43598279.8738 | 43598279.8738 | 43598279.8738 | 43598279.8738 | 43598279.8738 | 43598279.8738
Costs |  | 6038958.7044 | 0 | 5931828.75 | 91201.867 | 93481.9137 | 95818.9615 | 98214.4356 | 100669.7965 | 103186.5414 | 105766.2049 | 108410.36 | 111120.619 | 113898.6345 | 116746.1004 | 119664.7529 | 122656.3717
Net Economic Benefit |  | 226940193.1021
Option 4
Weighted EUSE (MWh) |  |  | 7.6127 | 61.2216 | 0 | 0.0068524 | 0.0095512 | 0.0091869 | 0.012882 | 0.020969 | 0.025804 | 0.025804 | 0.025804 | 0.025804 | 0.025804 | 0.025804 | 0.025804
Weighted Cost of EUSE |  | 1937042.1403 | 240196.2197 | 1931664.4734 | 0 | 216.2079 | 301.3603 | 289.8652 | 406.4579 | 661.6089 | 814.1633 | 814.1633 | 814.1633 | 814.1633 | 814.1633 | 814.1633 | 814.1633
Benefits |  | 272155816.1689 | 0 | 0 | 8407464.7877 | 17307846.4547 | 20869011.0285 | 27029134.4559 | 30906772.5891 | 41953711.3335 | 51164727.9792 | 51164727.9792 | 51164727.9792 | 51164727.9792 | 51164727.9792 | 51164727.9792 | 51164727.9792
Costs |  | 11156992.2504 | 0 | 10959069.375 | 168495.6916 | 172708.0839 | 177025.786 | 181451.4307 | 185987.7164 | 190637.4094 | 195403.3446 | 200288.4282 | 205295.6389 | 210428.0299 | 215688.7306 | 221080.9489 | 226607.9726
Net Economic Benefit |  | 260998823.9184

## Cost-Benefit (Disc rate high)
VCR | 39440 |  | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
Discount Rate | 8.26%
Option costs | $2017 Real
Do Nothing
Weighted EUSE (MWh) |  |  | 7.6127 | 61.2216 | 266.4638 | 548.5568 | 661.426 | 856.6628 | 979.5632 | 1329.6898 | 1621.626 | 1621.626 | 1621.626 | 1621.626 | 1621.626 | 1621.626 | 1621.626
Weighted Cost of EUSE |  | 289773257.86 | 300245.2746 | 2414580.5918 | 10509330.9846 | 21635078.3283 | 26086640.486 | 33786780.4013 | 38633973.8088 | 52442966.1779 | 63956927.6781 | 63956927.6781 | 63956927.6781 | 63956927.6781 | 63956927.6781 | 63956927.6781 | 63956927.6781
Benefits |  | -289773257.86 | -300245.2746 | -2414580.5918 | -10509330.9846 | -21635078.3283 | -26086640.486 | -33786780.4013 | -38633973.8088 | -52442966.1779 | -63956927.6781 | -63956927.6781 | -63956927.6781 | -63956927.6781 | -63956927.6781 | -63956927.6781 | -63956927.6781
Costs |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Net Economic Benefit |  | -289773257.86
Option 1
Weighted EUSE (MWh) |  |  | 7.6127 | 61.2216 | 0.010864 | 0.031786 | 0.044041 | 0.85907 | 2.3245 | 6.7994 | 10.0316 | 10.0316 | 10.0316 | 10.0316 | 10.0316 | 10.0316 | 10.0316
Weighted Cost of EUSE |  | 3637756.008 | 300245.2746 | 2414580.5918 | 428.4832 | 1253.6266 | 1736.9939 | 33881.6291 | 91676.9799 | 268167.1858 | 395648.0728 | 395648.0728 | 395648.0728 | 395648.0728 | 395648.0728 | 395648.0728 | 395648.0728
Benefits |  | 286135501.852 | 0 | 0 | 10508902.5014 | 21633824.7017 | 26084903.4921 | 33752898.7722 | 38542296.8289 | 52174798.9922 | 63561279.6053 | 63561279.6053 | 63561279.6053 | 63561279.6053 | 63561279.6053 | 63561279.6053 | 63561279.6053
Costs |  | 13321436.5598 | 0 | 13746377.5 | 211350.5541 | 216634.3179 | 222050.1759 | 227601.4303 | 233291.466 | 239123.7527 | 245101.8465 | 251229.3926 | 257510.1275 | 263947.8806 | 270546.5777 | 277310.2421 | 284242.9982
Net Economic Benefit |  | 272814065.2922
Option 2
Weighted EUSE (MWh) |  |  | 7.6127 | 61.2216 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 0.00034
Weighted Cost of EUSE |  | 2337556.2335 | 300245.2746 | 2414580.5918 | 0 | 0 | 0 | 0 | 0 | 0 | 13.4096 | 13.4096 | 13.4096 | 13.4096 | 13.4096 | 13.4096 | 13.4096
Benefits |  | 287435701.6265 | 0 | 0 | 10509330.9846 | 21635078.3283 | 26086640.486 | 33786780.4013 | 38633973.8088 | 52442966.1779 | 63956914.2685 | 63956914.2685 | 63956914.2685 | 63956914.2685 | 63956914.2685 | 63956914.2685 | 63956914.2685
Costs |  | 15655030.6381 | 0 | 16154410 | 248374.0537 | 254583.4051 | 260947.9902 | 267471.69 | 274158.4822 | 281012.4443 | 288037.7554 | 295238.6993 | 302619.6668 | 310185.1584 | 317939.7874 | 325889.2821 | 334037.5045
Net Economic Benefit |  | 271780670.9884
Option 3
Weighted EUSE (MWh) |  |  | 7.6127 | 61.2216 | 55.8482 | 44.4638 | 69.4326 | 107.3405 | 135.3571 | 231.7711 | 239.8346 | 239.8346 | 239.8346 | 239.8346 | 239.8346 | 239.8346 | 239.8346
Weighted Cost of EUSE |  | 43598165.5876 | 300245.2746 | 2414580.5918 | 2202653.6663 | 1753653.0303 | 2738419.8656 | 4233509.1849 | 5338485.6937 | 9141050.4345 | 9459077.8359 | 9459077.8359 | 9459077.8359 | 9459077.8359 | 9459077.8359 | 9459077.8359 | 9459077.8359
Benefits |  | 246175092.2724 | 0 | 0 | 8306677.3184 | 19881425.298 | 23348220.6204 | 29553271.2164 | 33295488.1151 | 43301915.7434 | 54497849.8423 | 54497849.8423 | 54497849.8423 | 54497849.8423 | 54497849.8423 | 54497849.8423 | 54497849.8423
Costs |  | 5748458.4849 | 0 | 5931828.75 | 91201.867 | 93481.9137 | 95818.9615 | 98214.4356 | 100669.7965 | 103186.5414 | 105766.2049 | 108410.36 | 111120.619 | 113898.6345 | 116746.1004 | 119664.7529 | 122656.3717
Net Economic Benefit |  | 240426633.7875
Option 4
Weighted EUSE (MWh) |  |  | 7.6127 | 61.2216 | 0 | 0.0068524 | 0.0095512 | 0.0091869 | 0.012882 | 0.020969 | 0.025804 | 0.025804 | 0.025804 | 0.025804 | 0.025804 | 0.025804 | 0.025804
Weighted Cost of EUSE |  | 2341707.7831 | 300245.2746 | 2414580.5918 | 0 | 270.2599 | 376.7003 | 362.3314 | 508.0724 | 827.0111 | 1017.7041 | 1017.7041 | 1017.7041 | 1017.7041 | 1017.7041 | 1017.7041 | 1017.7041
Benefits |  | 287431550.0769 | 0 | 0 | 10509330.9846 | 21634808.0684 | 26086263.7857 | 33786418.0699 | 38633465.7364 | 52442139.1668 | 63955909.974 | 63955909.974 | 63955909.974 | 63955909.974 | 63955909.974 | 63955909.974 | 63955909.974
Costs |  | 10620292.3231 | 0 | 10959069.375 | 168495.6916 | 172708.0839 | 177025.786 | 181451.4307 | 185987.7164 | 190637.4094 | 195403.3446 | 200288.4282 | 205295.6389 | 210428.0299 | 215688.7306 | 221080.9489 | 226607.9726
Net Economic Benefit |  | 276811257.7538

## Cost-Benefit (cost+30%)
VCR | 39440 |  | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
Discount Rate | 6.37%
Cost Sensitivity | 1.3
Do Nothing
Weighted EUSE (MWh) |  |  | 7.6127 | 61.2216 | 266.4638 | 548.5568 | 661.426 | 856.6628 | 979.5632 | 1329.6898 | 1621.626 | 1621.626 | 1621.626 | 1621.626 | 1621.626 | 1621.626 | 1621.626
Weighted Cost of EUSE |  | 342616072.8865 | 300245.2746 | 2414580.5918 | 10509330.9846 | 21635078.3283 | 26086640.486 | 33786780.4013 | 38633973.8088 | 52442966.1779 | 63956927.6781 | 63956927.6781 | 63956927.6781 | 63956927.6781 | 63956927.6781 | 63956927.6781 | 63956927.6781
Benefits |  | -342616072.8865 | -300245.2746 | -2414580.5918 | -10509330.9846 | -21635078.3283 | -26086640.486 | -33786780.4013 | -38633973.8088 | -52442966.1779 | -63956927.6781 | -63956927.6781 | -63956927.6781 | -63956927.6781 | -63956927.6781 | -63956927.6781 | -63956927.6781
Costs |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Net Economic Benefit |  | -342616072.8865
Option 1
Weighted EUSE (MWh) |  |  | 7.6127 | 61.2216 | 0.010864 | 0.031786 | 0.044041 | 0.85907 | 2.3245 | 6.7994 | 10.0316 | 10.0316 | 10.0316 | 10.0316 | 10.0316 | 10.0316 | 10.0316
Weighted Cost of EUSE |  | 3995538.1943 | 300245.2746 | 2414580.5918 | 428.4832 | 1253.6266 | 1736.9939 | 33881.6291 | 91676.9799 | 268167.1858 | 395648.0728 | 395648.0728 | 395648.0728 | 395648.0728 | 395648.0728 | 395648.0728 | 395648.0728
Benefits |  | 338620534.6922 | 0 | 0 | 10508902.5014 | 21633824.7017 | 26084903.4921 | 33752898.7722 | 38542296.8289 | 52174798.9922 | 63561279.6053 | 63561279.6053 | 63561279.6053 | 63561279.6053 | 63561279.6053 | 63561279.6053 | 63561279.6053
Costs |  | 18193031.5968 | 0 | 17870290.75 | 274755.7203 | 281624.6133 | 288665.2286 | 295881.8593 | 303278.9058 | 310860.8785 | 318632.4004 | 326598.2104 | 334763.1657 | 343132.2448 | 351710.551 | 360503.3147 | 369515.8976
Net Economic Benefit |  | 320427503.0954
Option 2
Weighted EUSE (MWh) |  |  | 7.6127 | 61.2216 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 0.00034
Weighted Cost of EUSE |  | 2416354.1611 | 300245.2746 | 2414580.5918 | 0 | 0 | 0 | 0 | 0 | 0 | 13.4096 | 13.4096 | 13.4096 | 13.4096 | 13.4096 | 13.4096 | 13.4096
Benefits |  | 340199718.7254 | 0 | 0 | 10509330.9846 | 21635078.3283 | 26086640.486 | 33786780.4013 | 38633973.8088 | 52442966.1779 | 63956914.2685 | 63956914.2685 | 63956914.2685 | 63956914.2685 | 63956914.2685 | 63956914.2685 | 63956914.2685
Costs |  | 21380011.8139 | 0 | 21000733 | 322886.2699 | 330958.4266 | 339232.3873 | 347713.197 | 356406.0269 | 365316.1776 | 374449.082 | 383810.3091 | 393405.5668 | 403240.706 | 413321.7236 | 423656.0667 | 434248.7558
Net Economic Benefit |  | 318819706.9115
Option 3
Weighted EUSE (MWh) |  |  | 7.6127 | 61.2216 | 55.8482 | 44.4638 | 69.4326 | 107.3405 | 135.3571 | 231.7711 | 239.8346 | 239.8346 | 239.8346 | 239.8346 | 239.8346 | 239.8346 | 239.8346
Weighted Cost of EUSE |  | 51392133.1283 | 300245.2746 | 2414580.5918 | 2202653.6663 | 1753653.0303 | 2738419.8656 | 4233509.1849 | 5338485.6937 | 9141050.4345 | 9459077.8359 | 9459077.8359 | 9459077.8359 | 9459077.8359 | 9459077.8359 | 9459077.8359 | 9459077.8359
Benefits |  | 291223939.7582 | 0 | 0 | 8306677.3184 | 19881425.298 | 23348220.6204 | 29553271.2164 | 33295488.1151 | 43301915.7434 | 54497849.8423 | 54497849.8423 | 54497849.8423 | 54497849.8423 | 54497849.8423 | 54497849.8423 | 54497849.8423
Costs |  | 7850646.3158 | 0 | 7711377.375 | 118562.4271 | 121526.4878 | 124564.65 | 127678.7663 | 130870.7354 | 134142.5038 | 137496.0664 | 140933.4681 | 144456.8048 | 148068.2249 | 151769.9305 | 155564.1788 | 159453.2832
Net Economic Benefit |  | 283373293.4424
Option 4
Weighted EUSE (MWh) |  |  | 7.6127 | 61.2216 | 0 | 0.0068524 | 0.0095512 | 0.0091869 | 0.012882 | 0.020969 | 0.025804 | 0.025804 | 0.025804 | 0.025804 | 0.025804 | 0.025804 | 0.025804
Weighted Cost of EUSE |  | 2421302.6754 | 300245.2746 | 2414580.5918 | 0 | 270.2599 | 376.7003 | 362.3314 | 508.0724 | 827.0111 | 1017.7041 | 1017.7041 | 1017.7041 | 1017.7041 | 1017.7041 | 1017.7041 | 1017.7041
Benefits |  | 340194770.2111 | 0 | 0 | 10509330.9846 | 21634808.0684 | 26086263.7857 | 33786418.0699 | 38633465.7364 | 52442139.1668 | 63955909.974 | 63955909.974 | 63955909.974 | 63955909.974 | 63955909.974 | 63955909.974 | 63955909.974
Costs |  | 14504089.9256 | 0 | 14246790.1875 | 219044.3991 | 224520.5091 | 230133.5218 | 235886.8599 | 241784.0314 | 247828.6322 | 254024.348 | 260374.9567 | 266884.3306 | 273556.4389 | 280395.3498 | 287405.2336 | 294590.3644
Net Economic Benefit |  | 325690680.2855

## Cost-Benefit (cost-30%)
VCR | 39440 |  | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
Discount Rate | 6.37%
Cost Sensitivity | 0.7
Do Nothing
Weighted EUSE (MWh) |  |  | 7.6127 | 61.2216 | 266.4638 | 548.5568 | 661.426 | 856.6628 | 979.5632 | 1329.6898 | 1621.626 | 1621.626 | 1621.626 | 1621.626 | 1621.626 | 1621.626 | 1621.626
Weighted Cost of EUSE |  | 342616072.8865 | 300245.2746 | 2414580.5918 | 10509330.9846 | 21635078.3283 | 26086640.486 | 33786780.4013 | 38633973.8088 | 52442966.1779 | 63956927.6781 | 63956927.6781 | 63956927.6781 | 63956927.6781 | 63956927.6781 | 63956927.6781 | 63956927.6781
Benefits |  | -342616072.8865 | -300245.2746 | -2414580.5918 | -10509330.9846 | -21635078.3283 | -26086640.486 | -33786780.4013 | -38633973.8088 | -52442966.1779 | -63956927.6781 | -63956927.6781 | -63956927.6781 | -63956927.6781 | -63956927.6781 | -63956927.6781 | -63956927.6781
Costs |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Net Economic Benefit |  | -342616072.8865
Option 1
Weighted EUSE (MWh) |  |  | 7.6127 | 61.2216 | 0.010864 | 0.031786 | 0.044041 | 0.85907 | 2.3245 | 6.7994 | 10.0316 | 10.0316 | 10.0316 | 10.0316 | 10.0316 | 10.0316 | 10.0316
Weighted Cost of EUSE |  | 3995538.1943 | 300245.2746 | 2414580.5918 | 428.4832 | 1253.6266 | 1736.9939 | 33881.6291 | 91676.9799 | 268167.1858 | 395648.0728 | 395648.0728 | 395648.0728 | 395648.0728 | 395648.0728 | 395648.0728 | 395648.0728
Benefits |  | 338620534.6922 | 0 | 0 | 10508902.5014 | 21633824.7017 | 26084903.4921 | 33752898.7722 | 38542296.8289 | 52174798.9922 | 63561279.6053 | 63561279.6053 | 63561279.6053 | 63561279.6053 | 63561279.6053 | 63561279.6053 | 63561279.6053
Costs |  | 9796247.7829 | 0 | 9622464.25 | 147945.3878 | 151644.0225 | 155435.1231 | 159321.0012 | 163304.0262 | 167386.6269 | 171571.2925 | 175860.5749 | 180257.0892 | 184763.5165 | 189382.6044 | 194117.1695 | 198970.0987
Net Economic Benefit |  | 328824286.9093
Option 2
Weighted EUSE (MWh) |  |  | 7.6127 | 61.2216 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 0.00034
Weighted Cost of EUSE |  | 2416354.1611 | 300245.2746 | 2414580.5918 | 0 | 0 | 0 | 0 | 0 | 0 | 13.4096 | 13.4096 | 13.4096 | 13.4096 | 13.4096 | 13.4096 | 13.4096
Benefits |  | 340199718.7254 | 0 | 0 | 10509330.9846 | 21635078.3283 | 26086640.486 | 33786780.4013 | 38633973.8088 | 52442966.1779 | 63956914.2685 | 63956914.2685 | 63956914.2685 | 63956914.2685 | 63956914.2685 | 63956914.2685 | 63956914.2685
Costs |  | 11512314.0536 | 0 | 11308087 | 173861.8376 | 178208.3836 | 182663.5932 | 187230.183 | 191910.9376 | 196708.711 | 201626.4288 | 206667.0895 | 211833.7667 | 217129.6109 | 222557.8512 | 228122.4974 | 233826.2531
Net Economic Benefit |  | 328687404.6717
Option 3
Weighted EUSE (MWh) |  |  | 7.6127 | 61.2216 | 55.8482 | 44.4638 | 69.4326 | 107.3405 | 135.3571 | 231.7711 | 239.8346 | 239.8346 | 239.8346 | 239.8346 | 239.8346 | 239.8346 | 239.8346
Weighted Cost of EUSE |  | 51392133.1283 | 300245.2746 | 2414580.5918 | 2202653.6663 | 1753653.0303 | 2738419.8656 | 4233509.1849 | 5338485.6937 | 9141050.4345 | 9459077.8359 | 9459077.8359 | 9459077.8359 | 9459077.8359 | 9459077.8359 | 9459077.8359 | 9459077.8359
Benefits |  | 291223939.7582 | 0 | 0 | 8306677.3184 | 19881425.298 | 23348220.6204 | 29553271.2164 | 33295488.1151 | 43301915.7434 | 54497849.8423 | 54497849.8423 | 54497849.8423 | 54497849.8423 | 54497849.8423 | 54497849.8423 | 54497849.8423
Costs |  | 4227271.0931 | 0 | 4152280.125 | 63841.3069 | 65437.3396 | 67073.2731 | 68750.1049 | 70468.8575 | 72230.579 | 74036.3434 | 75887.252 | 77784.4333 | 79729.0442 | 81722.2703 | 83765.327 | 85859.4602
Net Economic Benefit |  | 286996668.6651
Option 4
Weighted EUSE (MWh) |  |  | 7.6127 | 61.2216 | 0 | 0.0068524 | 0.0095512 | 0.0091869 | 0.012882 | 0.020969 | 0.025804 | 0.025804 | 0.025804 | 0.025804 | 0.025804 | 0.025804 | 0.025804
Weighted Cost of EUSE |  | 2421302.6754 | 300245.2746 | 2414580.5918 | 0 | 270.2599 | 376.7003 | 362.3314 | 508.0724 | 827.0111 | 1017.7041 | 1017.7041 | 1017.7041 | 1017.7041 | 1017.7041 | 1017.7041 | 1017.7041
Benefits |  | 340194770.2111 | 0 | 0 | 10509330.9846 | 21634808.0684 | 26086263.7857 | 33786418.0699 | 38633465.7364 | 52442139.1668 | 63955909.974 | 63955909.974 | 63955909.974 | 63955909.974 | 63955909.974 | 63955909.974 | 63955909.974
Costs |  | 7809894.5753 | 0 | 7671348.5625 | 117946.9841 | 120895.6588 | 123918.0502 | 127016.0015 | 130191.4015 | 133446.1866 | 136782.3412 | 140201.8997 | 143706.9472 | 147299.6209 | 150982.1114 | 154756.6642 | 158625.5808
Net Economic Benefit |  | 332384875.6358