## Report summary Table
Table 8-2: Market benefits of augmentation options relative to the base case
Augmentation option | Total lifecycle project cost (2017-2032) ($M, real 2017) | NPV of net economic benefit (2017-2032 ) $M | Project ranking
Base Case - Do Nothing |  |  | N/A
Option 1 - Reconductor the 66kV loop with higher capacity conductor in 2019 | 13.084 | 250.396 | 2
Option 2 - Install a new KTS-MAT 66kV line to form a four legged 66kV loop in 2019 | 15.376 | 249.3533 | 3
Option 3 - Split the existing 66kV loop by installing one additional 66kV line in 2019 | 5.646 | 211.2243 | 4
Option 4 - Split the existing 66kV loop by installing two additional 66kV lines in 2019 | 10.431 | 254.639 | 1

## Sensitivity Analysis Summary
Option | Net Economic Benefit ($) | Rank | Net Economic Benefit ($) | Rank | Net Economic Benefit ($) | Rank | Net Economic Benefit ($) | Rank | Net Economic Benefit ($) | Rank | Net Economic Benefit ($) | Rank | Average Net Economic benefit ($) | Overall Rank of Feasible Options | Include Option in Ranking?
| Base (planning) scenario |  | VCR High (+20%) |  | VCR Low (-20%) |  | Discount Rate High (8.26%) |  | Investment Cost High (+30%) |  | Investment Cost Low (-30%)
Option 1 | 250395954.2084 | 2 | 303560996.7623 | 2 | 197709117.9449 | 2 | 205571679.5603 | 2 | 246436665.4466 | 2 | 254833449.2605 | 2 | 243084643.8638 | 2 | yes
Option 2 | 249353336.9076 | 3 | 302800160.6501 | 3 | 196384719.4555 | 3 | 204388618.5107 | 3 | 244658591.1726 | 3 | 254526288.9329 | 3 | 242018619.2716 | 3 | yes
Option 3 | 211224349.2725 | 4 | 254963934.6422 | 4 | 167962970.1933 | 4 | 173431596.6419 | 4 | 209651764.8064 | 4 | 213275140.0291 | 4 | 205084959.2642 | 4 | yes
Option 4 | 254639017.1628 | 1 | 308085142.8197 | 1 | 201671097.7963 | 1 | 209420510.8364 | 1 | 251531022.6329 | 1 | 258225217.9832 | 1 | 247262001.5386 | 1 | yes

## Opt 3 - Economic timing
Discount Rate | 6.37%
PV cost (Capital and Operational) $ | 6038958.7044
Year | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
Base case ( Do nothing) EUSE | 17073.4658 | 252374.0468 | 1137704.0495 | 2095375.6437 | 5050069.1492 | 11707955.9042 | 20226706.779 | 38555752.7677 | 63956927.6781 | 63956927.6781 | 63956927.6781 | 63956927.6781 | 63956927.6781 | 63956927.6781 | 63956927.6781
Annualised benefits after implementation of Option 3 ($) | -17073.4658 | -252374.0468 | 1137704.0495 | 2095375.6437 | 5050069.1492 | 11707955.9042 | 20226706.779 | 38555752.7677 | 63956927.6781 | 63956927.6781 | 63956927.6781 | 63956927.6781 | 63956927.6781 | 63956927.6781 | 63956927.6781
Annualised benefits after implementation of Option 3 ($M) | -0.017073 | -0.25237 | 1.1377 | 2.0954 | 5.0501 | 11.708 | 20.2267 | 38.5558 | 63.9569 | 63.9569 | 63.9569 | 63.9569 | 63.9569 | 63.9569 | 63.9569
Annualised cost for Option 3 ($) | 403064.6864 | 403064.6864 | 403064.6864 | 403064.6864 | 403064.6864 | 403064.6864 | 403064.6864 | 403064.6864 | 403064.6864 | 403064.6864 | 403064.6864 | 403064.6864 | 403064.6864 | 403064.6864 | 403064.6864
Annualised cost for Option 3 ($M) | 0.40306 | 0.40306 | 0.40306 | 0.40306 | 0.40306 | 0.40306 | 0.40306 | 0.40306 | 0.40306 | 0.40306 | 0.40306 | 0.40306 | 0.40306 | 0.40306 | 0.40306

## Option Costs
Year |  | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
Discount Rate | 6.37%
Inflation Rate | 2.5%
O&M cost | 1.5%
Option 1 |  | 0 | 13746377.5 | 211350.5541 | 216634.3179 | 222050.1759 | 227601.4303 | 233291.466 | 239123.7527 | 245101.8465 | 251229.3926 | 257510.1275 | 263947.8806 | 270546.5777 | 277310.2421 | 284242.9982
Capital |  | 0 | 13746377.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Operational |  | 0 | 0 | 211350.5541 | 216634.3179 | 222050.1759 | 227601.4303 | 233291.466 | 239123.7527 | 245101.8465 | 251229.3926 | 257510.1275 | 263947.8806 | 270546.5777 | 277310.2421 | 284242.9982
Option 2 |  | 0 | 16154410 | 248374.0537 | 254583.4051 | 260947.9902 | 267471.69 | 274158.4822 | 281012.4443 | 288037.7554 | 295238.6993 | 302619.6668 | 310185.1584 | 317939.7874 | 325889.2821 | 334037.5045
Capital |  | 0 | 16154410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2
Operational |  | 0 | 0 | 248374.0537 | 254583.4051 | 260947.9902 | 267471.69 | 274158.4822 | 281012.4443 | 288037.7554 | 295238.6993 | 302619.6668 | 310185.1584 | 317939.7874 | 325888.2821 | 334035.5045
Option 3 |  | 0 | 5931828.75 | 91201.867 | 93481.9137 | 95818.9615 | 98214.4356 | 100669.7965 | 103186.5414 | 105766.2049 | 108410.36 | 111120.619 | 113898.6345 | 116746.1004 | 119664.7529 | 122656.3717
Capital |  | 0 | 5931828.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Operational |  | 0 | 0 | 91201.867 | 93481.9137 | 95818.9615 | 98214.4356 | 100669.7965 | 103186.5414 | 105766.2049 | 108410.36 | 111120.619 | 113898.6345 | 116746.1004 | 119664.7529 | 122656.3717
Option 4 |  | 0 | 10959069.375 | 168495.6916 | 172708.0839 | 177025.786 | 181451.4307 | 185987.7164 | 190637.4094 | 195403.3446 | 200288.4282 | 205295.6389 | 210428.0299 | 215688.7306 | 221080.9489 | 226607.9726
Capital |  | 0 | 10959069.375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Operational |  | 0 | 0 | 168495.6916 | 172708.0839 | 177025.786 | 181451.4307 | 185987.7164 | 190637.4094 | 195403.3446 | 200288.4282 | 205295.6389 | 210428.0299 | 215688.7306 | 221080.9489 | 226607.9726
| Real $2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
Option 1 - Reconductor the 66kV loop with higher capacity conductor in 2019 | 13084000 | 13411100 | 13746377.5 | 14090036.9375 | 14442287.8609 | 14803345.0575 | 15173428.6839 | 15552764.401 | 15941583.511 | 16340123.0988 | 16748626.1763 | 17167341.8307 | 17596525.3764 | 18036438.5108 | 18487349.4736 | 18949533.2105
Option 2 - Install a new KTS-MAT 66kV line to form a four legged 66kV loop in 2019 | 15376000 | 15760400 | 16154410 | 16558270.25 | 16972227.0062 | 17396532.6814 | 17831445.9984 | 18277232.1484 | 18734162.9521 | 19202517.0259 | 19682579.9516 | 20174644.4504 | 20679010.5616 | 21195985.8257 | 21725885.4713 | 22269032.6081
Option 3 - Split the existing 66kV loop by installing one additional 66kV line in 2019 | 5646000 | 5787150 | 5931828.75 | 6080124.4687 | 6232127.5805 | 6387930.77 | 6547629.0392 | 6711319.7652 | 6879102.7593 | 7051080.3283 | 7227357.3365 | 7408041.2699 | 7593242.3017 | 7783073.3592 | 7977650.1932 | 8177091.448
Option 4 - Split the existing 66kV loop by installing two additional 66kV lines in 2019 | 10431000 | 10691775 | 10959069.375 | 11233046.1094 | 11513872.2621 | 11801719.0687 | 12096762.0454 | 12399181.0965 | 12709160.6239 | 13026889.6395 | 13352561.8805 | 13686375.9275 | 14028535.3257 | 14379248.7089 | 14738729.9266 | 15107198.1747

## Cost-Benefit (BASE)
VCR | 39440 |  | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
Discount Rate | 6.37%
Option costs | $2017 Real
Do Nothing
Weighted EUSE (MWh) |  |  | 0.4329 | 6.3989 | 28.8465 | 53.1282 | 128.0443 | 296.8549 | 512.8475 | 977.5799 | 1621.626 | 1621.626 | 1621.626 | 1621.626 | 1621.626 | 1621.626 | 1621.626
Weighted Cost of EUSE |  |  | 17073.4658 | 252374.0468 | 1137704.0495 | 2095375.6437 | 5050069.1492 | 11707955.9042 | 20226706.779 | 38555752.7677 | 63956927.6781 | 63956927.6781 | 63956927.6781 | 63956927.6781 | 63956927.6781 | 63956927.6781 | 63956927.6781
Benefits |  | -266277751.2125 | -17073.4658 | -252374.0468 | -1137704.0495 | -2095375.6437 | -5050069.1492 | -11707955.9042 | -20226706.779 | -38555752.7677 | -63956927.6781 | -63956927.6781 | -63956927.6781 | -63956927.6781 | -63956927.6781 | -63956927.6781 | -63956927.6781
Costs |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Net Economic Benefit |  | -266277751.2125
Option 1
Weighted EUSE (MWh) |  |  | 0.4329 | 6.3989 | 0.00018346 | 0.00072561 | 0.0035361 | 0.013887 | 0.030374 | 3.2231 | 10.0316 | 10.0316 | 10.0316 | 10.0316 | 10.0316 | 10.0316 | 10.0316
Weighted Cost of EUSE |  | 1648054.169 | 17073.4658 | 252374.0468 | 7.2355 | 28.618 | 139.4619 | 547.7109 | 1197.9528 | 127120.9211 | 395648.0728 | 395648.0728 | 395648.0728 | 395648.0728 | 395648.0728 | 395648.0728 | 395648.0728
Benefits |  | 264390593.8982 | -17073.4658 | -252374.0468 | 1137696.814 | 2095347.0258 | 5049929.6873 | 11707408.1934 | 20225508.8263 | 38428631.8466 | 63561279.6053 | 63561279.6053 | 63561279.6053 | 63561279.6053 | 63561279.6053 | 63561279.6053 | 63561279.6053
Costs |  | 13994639.6898 | 0 | 13746377.5 | 211350.5541 | 216634.3179 | 222050.1759 | 227601.4303 | 233291.466 | 239123.7527 | 245101.8465 | 251229.3926 | 257510.1275 | 263947.8806 | 270546.5777 | 277310.2421 | 284242.9982
Net Economic Benefit |  | 250395954.2084
Option 2
Weighted EUSE (MWh) |  |  | 0.4329 | 6.3989 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 0.00034
Weighted Cost of EUSE |  | 239148.226 | 17073.4658 | 252374.0468 | 0 | 0 | 0 | 0 | 0 | 0 | 13.4096 | 13.4096 | 13.4096 | 13.4096 | 13.4096 | 13.4096 | 13.4096
Benefits |  | 265799499.8413 | -17073.4658 | -252374.0468 | 1137704.0495 | 2095375.6437 | 5050069.1492 | 11707955.9042 | 20226706.779 | 38555752.7677 | 63956914.2685 | 63956914.2685 | 63956914.2685 | 63956914.2685 | 63956914.2685 | 63956914.2685 | 63956914.2685
Costs |  | 16446162.9337 | 0 | 16154410 | 248374.0537 | 254583.4051 | 260947.9902 | 267471.69 | 274158.4822 | 281012.4443 | 288037.7554 | 295238.6993 | 302619.6668 | 310185.1584 | 317939.7874 | 325889.2821 | 334037.5045
Net Economic Benefit |  | 249353336.9076
Option 3
Weighted EUSE (MWh) |  |  | 0.4329 | 6.3989 | 51.0827 | 43.4734 | 66.3026 | 110.0232 | 138.4424 | 218.7113 | 239.8346 | 239.8346 | 239.8346 | 239.8346 | 239.8346 | 239.8346 | 239.8346
Weighted Cost of EUSE |  | 48775340.0903 | 17073.4658 | 252374.0468 | 2014702.3174 | 1714592.774 | 2614975.7385 | 4339316.8934 | 5460168.4993 | 8625974.3459 | 9459077.8359 | 9459077.8359 | 9459077.8359 | 9459077.8359 | 9459077.8359 | 9459077.8359 | 9459077.8359
Benefits |  | 217263307.977 | -17073.4658 | -252374.0468 | -876998.2679 | 380782.8697 | 2435093.4107 | 7368639.0108 | 14766538.2798 | 29929778.4218 | 54497849.8423 | 54497849.8423 | 54497849.8423 | 54497849.8423 | 54497849.8423 | 54497849.8423 | 54497849.8423
Costs |  | 6038958.7044 | 0 | 5931828.75 | 91201.867 | 93481.9137 | 95818.9615 | 98214.4356 | 100669.7965 | 103186.5414 | 105766.2049 | 108410.36 | 111120.619 | 113898.6345 | 116746.1004 | 119664.7529 | 122656.3717
Net Economic Benefit |  | 211224349.2725
Option 4
Weighted EUSE (MWh) |  |  | 0.4329 | 6.3989 | 0 | 0 | 0 | 0 | 0.00050914 | 0.0042025 | 0.025804 | 0.025804 | 0.025804 | 0.025804 | 0.025804 | 0.025804 | 0.025804
Weighted Cost of EUSE |  | 242638.654 | 17073.4658 | 252374.0468 | 0 | 0 | 0 | 0 | 20.0804 | 165.7453 | 1017.7041 | 1017.7041 | 1017.7041 | 1017.7041 | 1017.7041 | 1017.7041 | 1017.7041
Benefits |  | 265796009.4133 | -17073.4658 | -252374.0468 | 1137704.0495 | 2095375.6437 | 5050069.1492 | 11707955.9042 | 20226686.6986 | 38555587.0224 | 63955909.974 | 63955909.974 | 63955909.974 | 63955909.974 | 63955909.974 | 63955909.974 | 63955909.974
Costs |  | 11156992.2504 | 0 | 10959069.375 | 168495.6916 | 172708.0839 | 177025.786 | 181451.4307 | 185987.7164 | 190637.4094 | 195403.3446 | 200288.4282 | 205295.6389 | 210428.0299 | 215688.7306 | 221080.9489 | 226607.9726
Net Economic Benefit |  | 254639017.1628
Note: Option 3 addresses KTS-TMA-MAT EUSE but AW-PV becomes two legged loop making things worse during KTS-AW outage. Hence the NPV is -ve for this option
|  |  | 0.4329 | 6.3989 | 51.0827 | 43.4734 | 66.3026 | 110.0232 | 138.4424 | 218.7113 | 239.8346 | 239.8346 | 239.8346 | 239.8346 | 239.8346 | 239.8346 | 239.8346

## Cost-Benefit (VCR+20%)
VCR | 47328 |  | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
Discount Rate | 6.37%
Option costs | $2017 Real
Do Nothing
Weighted EUSE (MWh) |  |  | 0.4329 | 6.3989 | 28.8465 | 53.1282 | 128.0443 | 296.8549 | 512.8475 | 977.5799 | 1621.626 | 1621.626 | 1621.626 | 1621.626 | 1621.626 | 1621.626 | 1621.626
Weighted Cost of EUSE |  | 319533301.455 | 20488.1589 | 302848.8562 | 1365244.8594 | 2514450.7725 | 6060082.9791 | 14049547.0851 | 24272048.1348 | 46266903.3212 | 76748313.2138 | 76748313.2138 | 76748313.2138 | 76748313.2138 | 76748313.2138 | 76748313.2138 | 76748313.2138
Benefits |  | -319533301.455 | -20488.1589 | -302848.8562 | -1365244.8594 | -2514450.7725 | -6060082.9791 | -14049547.0851 | -24272048.1348 | -46266903.3212 | -76748313.2138 | -76748313.2138 | -76748313.2138 | -76748313.2138 | -76748313.2138 | -76748313.2138 | -76748313.2138
Costs |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Net Economic Benefit |  | -319533301.455
Option 1
Weighted EUSE (MWh) |  |  | 0.4329 | 6.3989 | 0.00018346 | 0.00072561 | 0.0035361 | 0.013887 | 0.030374 | 3.2231 | 10.0316 | 10.0316 | 10.0316 | 10.0316 | 10.0316 | 10.0316 | 10.0316
Weighted Cost of EUSE |  | 1977665.0029 | 20488.1589 | 302848.8562 | 8.6826 | 34.3416 | 167.3542 | 657.253 | 1437.5433 | 152545.1054 | 474777.6874 | 474777.6874 | 474777.6874 | 474777.6874 | 474777.6874 | 474777.6874 | 474777.6874
Benefits |  | 317555636.4521 | 0 | 0 | 1365236.1768 | 2514416.4309 | 6059915.6248 | 14048889.832 | 24270610.5915 | 46114358.2159 | 76273535.5264 | 76273535.5264 | 76273535.5264 | 76273535.5264 | 76273535.5264 | 76273535.5264 | 76273535.5264
Costs |  | 13994639.6898 | 0 | 13746377.5 | 211350.5541 | 216634.3179 | 222050.1759 | 227601.4303 | 233291.466 | 239123.7527 | 245101.8465 | 251229.3926 | 257510.1275 | 263947.8806 | 270546.5777 | 277310.2421 | 284242.9982
Net Economic Benefit |  | 303560996.7623
Option 2
Weighted EUSE (MWh) |  |  | 0.4329 | 6.3989 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 0.00034
Weighted Cost of EUSE |  | 286977.8711 | 20488.1589 | 302848.8562 | 0 | 0 | 0 | 0 | 0 | 0 | 16.0915 | 16.0915 | 16.0915 | 16.0915 | 16.0915 | 16.0915 | 16.0915
Benefits |  | 319246323.5838 | 0 | 0 | 1365244.8594 | 2514450.7725 | 6060082.9791 | 14049547.0851 | 24272048.1348 | 46266903.3212 | 76748297.1222 | 76748297.1222 | 76748297.1222 | 76748297.1222 | 76748297.1222 | 76748297.1222 | 76748297.1222
Costs |  | 16446162.9337 | 0 | 16154410 | 248374.0537 | 254583.4051 | 260947.9902 | 267471.69 | 274158.4822 | 281012.4443 | 288037.7554 | 295238.6993 | 302619.6668 | 310185.1584 | 317939.7874 | 325889.2821 | 334037.5045
Net Economic Benefit |  | 302800160.6501
Option 3
Weighted EUSE (MWh) |  |  | 0.4329 | 6.3989 | 51.0827 | 43.4734 | 66.3026 | 110.0232 | 138.4424 | 218.7113 | 239.8346 | 239.8346 | 239.8346 | 239.8346 | 239.8346 | 239.8346 | 239.8346
Weighted Cost of EUSE |  | 58530408.1084 | 20488.1589 | 302848.8562 | 2417642.7809 | 2057511.3288 | 3137970.8862 | 5207180.2721 | 6552202.1991 | 10351169.215 | 11350893.403 | 11350893.403 | 11350893.403 | 11350893.403 | 11350893.403 | 11350893.403 | 11350893.403
Benefits |  | 261002893.3466 | 0 | 0 | -1052397.9215 | 456939.4437 | 2922112.0928 | 8842366.813 | 17719845.9357 | 35915734.1062 | 65397419.8107 | 65397419.8107 | 65397419.8107 | 65397419.8107 | 65397419.8107 | 65397419.8107 | 65397419.8107
Costs |  | 6038958.7044 | 0 | 5931828.75 | 91201.867 | 93481.9137 | 95818.9615 | 98214.4356 | 100669.7965 | 103186.5414 | 105766.2049 | 108410.36 | 111120.619 | 113898.6345 | 116746.1004 | 119664.7529 | 122656.3717
Net Economic Benefit |  | 254963934.6422
Option 4
Weighted EUSE (MWh) |  |  | 0.4329 | 6.3989 | 0 | 0 | 0 | 0 | 0.00050914 | 0.0042025 | 0.025804 | 0.025804 | 0.025804 | 0.025804 | 0.025804 | 0.025804 | 0.025804
Weighted Cost of EUSE |  | 291166.3848 | 20488.1589 | 302848.8562 | 0 | 0 | 0 | 0 | 24.0965 | 198.8944 | 1221.2449 | 1221.2449 | 1221.2449 | 1221.2449 | 1221.2449 | 1221.2449 | 1221.2449
Benefits |  | 319242135.0702 | 0 | 0 | 1365244.8594 | 2514450.7725 | 6060082.9791 | 14049547.0851 | 24272024.0383 | 46266704.4268 | 76747091.9688 | 76747091.9688 | 76747091.9688 | 76747091.9688 | 76747091.9688 | 76747091.9688 | 76747091.9688
Costs |  | 11156992.2504 | 0 | 10959069.375 | 168495.6916 | 172708.0839 | 177025.786 | 181451.4307 | 185987.7164 | 190637.4094 | 195403.3446 | 200288.4282 | 205295.6389 | 210428.0299 | 215688.7306 | 221080.9489 | 226607.9726
Net Economic Benefit |  | 308085142.8197

## Cost-Benefit (VCR-20%)
VCR | 31552 |  | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
Discount Rate | 6.37%
Option costs | $2017 Real
Do Nothing
Weighted EUSE (MWh) |  |  | 0.4329 | 6.3989 | 28.8465 | 53.1282 | 128.0443 | 296.8549 | 512.8475 | 977.5799 | 1621.626 | 1621.626 | 1621.626 | 1621.626 | 1621.626 | 1621.626 | 1621.626
Weighted Cost of EUSE |  | 213022200.97 | 13658.7726 | 201899.2374 | 910163.2396 | 1676300.515 | 4040055.3194 | 9366364.7234 | 16181365.4232 | 30844602.2142 | 51165542.1425 | 51165542.1425 | 51165542.1425 | 51165542.1425 | 51165542.1425 | 51165542.1425 | 51165542.1425
Benefits |  | -213022200.97 | -13658.7726 | -201899.2374 | -910163.2396 | -1676300.515 | -4040055.3194 | -9366364.7234 | -16181365.4232 | -30844602.2142 | -51165542.1425 | -51165542.1425 | -51165542.1425 | -51165542.1425 | -51165542.1425 | -51165542.1425 | -51165542.1425
Costs |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Net Economic Benefit |  | -213022200.97
Option 1
Weighted EUSE (MWh) |  |  | 0.4329 | 6.3989 | 0.00018346 | 0.00072561 | 0.0035361 | 0.013887 | 0.030374 | 3.2231 | 10.0316 | 10.0316 | 10.0316 | 10.0316 | 10.0316 | 10.0316 | 10.0316
Weighted Cost of EUSE |  | 1318443.3352 | 13658.7726 | 201899.2374 | 5.7884 | 22.8944 | 111.5695 | 438.1687 | 958.3622 | 101696.7369 | 316518.4583 | 316518.4583 | 316518.4583 | 316518.4583 | 316518.4583 | 316518.4583 | 316518.4583
Benefits |  | 211703757.6347 | 0 | 0 | 910157.4512 | 1676277.6206 | 4039943.7499 | 9365926.5547 | 16180407.061 | 30742905.4773 | 50849023.6842 | 50849023.6842 | 50849023.6842 | 50849023.6842 | 50849023.6842 | 50849023.6842 | 50849023.6842
Costs |  | 13994639.6898 | 0 | 13746377.5 | 211350.5541 | 216634.3179 | 222050.1759 | 227601.4303 | 233291.466 | 239123.7527 | 245101.8465 | 251229.3926 | 257510.1275 | 263947.8806 | 270546.5777 | 277310.2421 | 284242.9982
Net Economic Benefit |  | 197709117.9449
Option 2
Weighted EUSE (MWh) |  |  | 0.4329 | 6.3989 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 0.00034
Weighted Cost of EUSE |  | 191318.5808 | 13658.7726 | 201899.2374 | 0 | 0 | 0 | 0 | 0 | 0 | 10.7277 | 10.7277 | 10.7277 | 10.7277 | 10.7277 | 10.7277 | 10.7277
Benefits |  | 212830882.3892 | 0 | 0 | 910163.2396 | 1676300.515 | 4040055.3194 | 9366364.7234 | 16181365.4232 | 30844602.2142 | 51165531.4148 | 51165531.4148 | 51165531.4148 | 51165531.4148 | 51165531.4148 | 51165531.4148 | 51165531.4148
Costs |  | 16446162.9337 | 0 | 16154410 | 248374.0537 | 254583.4051 | 260947.9902 | 267471.69 | 274158.4822 | 281012.4443 | 288037.7554 | 295238.6993 | 302619.6668 | 310185.1584 | 317939.7874 | 325889.2821 | 334037.5045
Net Economic Benefit |  | 196384719.4555
Option 3
Weighted EUSE (MWh) |  |  | 0.4329 | 6.3989 | 51.0827 | 43.4734 | 66.3026 | 110.0232 | 138.4424 | 218.7113 | 239.8346 | 239.8346 | 239.8346 | 239.8346 | 239.8346 | 239.8346 | 239.8346
Weighted Cost of EUSE |  | 39020272.0722 | 13658.7726 | 201899.2374 | 1611761.8539 | 1371674.2192 | 2091980.5908 | 3471453.5147 | 4368134.7994 | 6900779.4767 | 7567262.2687 | 7567262.2687 | 7567262.2687 | 7567262.2687 | 7567262.2687 | 7567262.2687 | 7567262.2687
Benefits |  | 174001928.8977 | 0 | 0 | -701598.6143 | 304626.2958 | 1948074.7286 | 5894911.2086 | 11813230.6238 | 23943822.7375 | 43598279.8738 | 43598279.8738 | 43598279.8738 | 43598279.8738 | 43598279.8738 | 43598279.8738 | 43598279.8738
Costs |  | 6038958.7044 | 0 | 5931828.75 | 91201.867 | 93481.9137 | 95818.9615 | 98214.4356 | 100669.7965 | 103186.5414 | 105766.2049 | 108410.36 | 111120.619 | 113898.6345 | 116746.1004 | 119664.7529 | 122656.3717
Net Economic Benefit |  | 167962970.1933
Option 4
Weighted EUSE (MWh) |  |  | 0.4329 | 6.3989 | 0 | 0 | 0 | 0 | 0.00050914 | 0.0042025 | 0.025804 | 0.025804 | 0.025804 | 0.025804 | 0.025804 | 0.025804 | 0.025804
Weighted Cost of EUSE |  | 194110.9232 | 13658.7726 | 201899.2374 | 0 | 0 | 0 | 0 | 16.0644 | 132.5963 | 814.1633 | 814.1633 | 814.1633 | 814.1633 | 814.1633 | 814.1633 | 814.1633
Benefits |  | 212828090.0468 | 0 | 0 | 910163.2396 | 1676300.515 | 4040055.3194 | 9366364.7234 | 16181349.3589 | 30844469.6179 | 51164727.9792 | 51164727.9792 | 51164727.9792 | 51164727.9792 | 51164727.9792 | 51164727.9792 | 51164727.9792
Costs |  | 11156992.2504 | 0 | 10959069.375 | 168495.6916 | 172708.0839 | 177025.786 | 181451.4307 | 185987.7164 | 190637.4094 | 195403.3446 | 200288.4282 | 205295.6389 | 210428.0299 | 215688.7306 | 221080.9489 | 226607.9726
Net Economic Benefit |  | 201671097.7963

## Cost-Benefit (Disc rate high)
VCR | 39440 |  | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
Discount Rate | 8.26%
Option costs | $2017 Real
Do Nothing
Weighted EUSE (MWh) |  |  | 0.4329 | 6.3989 | 28.8465 | 53.1282 | 128.0443 | 296.8549 | 512.8475 | 977.5799 | 1621.626 | 1621.626 | 1621.626 | 1621.626 | 1621.626 | 1621.626 | 1621.626
Weighted Cost of EUSE |  | 220274788.6561 | 17073.4658 | 252374.0468 | 1137704.0495 | 2095375.6437 | 5050069.1492 | 11707955.9042 | 20226706.779 | 38555752.7677 | 63956927.6781 | 63956927.6781 | 63956927.6781 | 63956927.6781 | 63956927.6781 | 63956927.6781 | 63956927.6781
Benefits |  | -220274788.6561 | -17073.4658 | -252374.0468 | -1137704.0495 | -2095375.6437 | -5050069.1492 | -11707955.9042 | -20226706.779 | -38555752.7677 | -63956927.6781 | -63956927.6781 | -63956927.6781 | -63956927.6781 | -63956927.6781 | -63956927.6781 | -63956927.6781
Costs |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Net Economic Benefit |  | -220274788.6561
Option 1
Weighted EUSE (MWh) |  |  | 0.4329 | 6.3989 | 0.00018346 | 0.00072561 | 0.0035361 | 0.013887 | 0.030374 | 3.2231 | 10.0316 | 10.0316 | 10.0316 | 10.0316 | 10.0316 | 10.0316 | 10.0316
Weighted Cost of EUSE |  | 1381672.536 | 17073.4658 | 252374.0468 | 7.2355 | 28.618 | 139.4619 | 547.7109 | 1197.9528 | 127120.9211 | 395648.0728 | 395648.0728 | 395648.0728 | 395648.0728 | 395648.0728 | 395648.0728 | 395648.0728
Benefits |  | 218893116.1201 | 0 | 0 | 1137696.814 | 2095347.0258 | 5049929.6873 | 11707408.1934 | 20225508.8263 | 38428631.8466 | 63561279.6053 | 63561279.6053 | 63561279.6053 | 63561279.6053 | 63561279.6053 | 63561279.6053 | 63561279.6053
Costs |  | 13321436.5598 | 0 | 13746377.5 | 211350.5541 | 216634.3179 | 222050.1759 | 227601.4303 | 233291.466 | 239123.7527 | 245101.8465 | 251229.3926 | 257510.1275 | 263947.8806 | 270546.5777 | 277310.2421 | 284242.9982
Net Economic Benefit |  | 205571679.5603
Option 2
Weighted EUSE (MWh) |  |  | 0.4329 | 6.3989 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 0.00034
Weighted Cost of EUSE |  | 231139.5073 | 17073.4658 | 252374.0468 | 0 | 0 | 0 | 0 | 0 | 0 | 13.4096 | 13.4096 | 13.4096 | 13.4096 | 13.4096 | 13.4096 | 13.4096
Benefits |  | 220043649.1488 | 0 | 0 | 1137704.0495 | 2095375.6437 | 5050069.1492 | 11707955.9042 | 20226706.779 | 38555752.7677 | 63956914.2685 | 63956914.2685 | 63956914.2685 | 63956914.2685 | 63956914.2685 | 63956914.2685 | 63956914.2685
Costs |  | 15655030.6381 | 0 | 16154410 | 248374.0537 | 254583.4051 | 260947.9902 | 267471.69 | 274158.4822 | 281012.4443 | 288037.7554 | 295238.6993 | 302619.6668 | 310185.1584 | 317939.7874 | 325889.2821 | 334037.5045
Net Economic Benefit |  | 204388618.5107
Option 3
Weighted EUSE (MWh) |  |  | 0.4329 | 6.3989 | 51.0827 | 43.4734 | 66.3026 | 110.0232 | 138.4424 | 218.7113 | 239.8346 | 239.8346 | 239.8346 | 239.8346 | 239.8346 | 239.8346 | 239.8346
Weighted Cost of EUSE |  | 41094733.5292 | 17073.4658 | 252374.0468 | 2014702.3174 | 1714592.774 | 2614975.7385 | 4339316.8934 | 5460168.4993 | 8625974.3459 | 9459077.8359 | 9459077.8359 | 9459077.8359 | 9459077.8359 | 9459077.8359 | 9459077.8359 | 9459077.8359
Benefits |  | 179180055.1268 | 0 | 0 | -876998.2679 | 380782.8697 | 2435093.4107 | 7368639.0108 | 14766538.2798 | 29929778.4218 | 54497849.8423 | 54497849.8423 | 54497849.8423 | 54497849.8423 | 54497849.8423 | 54497849.8423 | 54497849.8423
Costs |  | 5748458.4849 | 0 | 5931828.75 | 91201.867 | 93481.9137 | 95818.9615 | 98214.4356 | 100669.7965 | 103186.5414 | 105766.2049 | 108410.36 | 111120.619 | 113898.6345 | 116746.1004 | 119664.7529 | 122656.3717
Net Economic Benefit |  | 173431596.6419
Option 4
Weighted EUSE (MWh) |  |  | 0.4329 | 6.3989 | 0 | 0 | 0 | 0 | 0.00050914 | 0.0042025 | 0.025804 | 0.025804 | 0.025804 | 0.025804 | 0.025804 | 0.025804 | 0.025804
Weighted Cost of EUSE |  | 233985.4965 | 17073.4658 | 252374.0468 | 0 | 0 | 0 | 0 | 20.0804 | 165.7453 | 1017.7041 | 1017.7041 | 1017.7041 | 1017.7041 | 1017.7041 | 1017.7041 | 1017.7041
Benefits |  | 220040803.1595 | 0 | 0 | 1137704.0495 | 2095375.6437 | 5050069.1492 | 11707955.9042 | 20226686.6986 | 38555587.0224 | 63955909.974 | 63955909.974 | 63955909.974 | 63955909.974 | 63955909.974 | 63955909.974 | 63955909.974
Costs |  | 10620292.3231 | 0 | 10959069.375 | 168495.6916 | 172708.0839 | 177025.786 | 181451.4307 | 185987.7164 | 190637.4094 | 195403.3446 | 200288.4282 | 205295.6389 | 210428.0299 | 215688.7306 | 221080.9489 | 226607.9726
Net Economic Benefit |  | 209420510.8364

## Cost-Benefit (cost+30%)
VCR | 39440 |  | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
Discount Rate | 6.37%
Cost Sensitivity | 1.3
Do Nothing
Weighted EUSE (MWh) |  |  | 0.4329 | 6.3989 | 28.8465 | 53.1282 | 128.0443 | 296.8549 | 512.8475 | 977.5799 | 1621.626 | 1621.626 | 1621.626 | 1621.626 | 1621.626 | 1621.626 | 1621.626
Weighted Cost of EUSE |  | 266277751.2125 | 17073.4658 | 252374.0468 | 1137704.0495 | 2095375.6437 | 5050069.1492 | 11707955.9042 | 20226706.779 | 38555752.7677 | 63956927.6781 | 63956927.6781 | 63956927.6781 | 63956927.6781 | 63956927.6781 | 63956927.6781 | 63956927.6781
Benefits |  | -266277751.2125 | -17073.4658 | -252374.0468 | -1137704.0495 | -2095375.6437 | -5050069.1492 | -11707955.9042 | -20226706.779 | -38555752.7677 | -63956927.6781 | -63956927.6781 | -63956927.6781 | -63956927.6781 | -63956927.6781 | -63956927.6781 | -63956927.6781
Costs |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Net Economic Benefit |  | -266277751.2125
Option 1
Weighted EUSE (MWh) |  |  | 0.4329 | 6.3989 | 0.00018346 | 0.00072561 | 0.0035361 | 0.013887 | 0.030374 | 3.2231 | 10.0316 | 10.0316 | 10.0316 | 10.0316 | 10.0316 | 10.0316 | 10.0316
Weighted Cost of EUSE |  | 1648054.169 | 17073.4658 | 252374.0468 | 7.2355 | 28.618 | 139.4619 | 547.7109 | 1197.9528 | 127120.9211 | 395648.0728 | 395648.0728 | 395648.0728 | 395648.0728 | 395648.0728 | 395648.0728 | 395648.0728
Benefits |  | 264629697.0434 | 0 | 0 | 1137696.814 | 2095347.0258 | 5049929.6873 | 11707408.1934 | 20225508.8263 | 38428631.8466 | 63561279.6053 | 63561279.6053 | 63561279.6053 | 63561279.6053 | 63561279.6053 | 63561279.6053 | 63561279.6053
Costs |  | 18193031.5968 | 0 | 17870290.75 | 274755.7203 | 281624.6133 | 288665.2286 | 295881.8593 | 303278.9058 | 310860.8785 | 318632.4004 | 326598.2104 | 334763.1657 | 343132.2448 | 351710.551 | 360503.3147 | 369515.8976
Net Economic Benefit |  | 246436665.4466
Option 2
Weighted EUSE (MWh) |  |  | 0.4329 | 6.3989 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 0.00034
Weighted Cost of EUSE |  | 239148.226 | 17073.4658 | 252374.0468 | 0 | 0 | 0 | 0 | 0 | 0 | 13.4096 | 13.4096 | 13.4096 | 13.4096 | 13.4096 | 13.4096 | 13.4096
Benefits |  | 266038602.9865 | 0 | 0 | 1137704.0495 | 2095375.6437 | 5050069.1492 | 11707955.9042 | 20226706.779 | 38555752.7677 | 63956914.2685 | 63956914.2685 | 63956914.2685 | 63956914.2685 | 63956914.2685 | 63956914.2685 | 63956914.2685
Costs |  | 21380011.8139 | 0 | 21000733 | 322886.2699 | 330958.4266 | 339232.3873 | 347713.197 | 356406.0269 | 365316.1776 | 374449.082 | 383810.3091 | 393405.5668 | 403240.706 | 413321.7236 | 423656.0667 | 434248.7558
Net Economic Benefit |  | 244658591.1726
Option 3
Weighted EUSE (MWh) |  |  | 0.4329 | 6.3989 | 51.0827 | 43.4734 | 66.3026 | 110.0232 | 138.4424 | 218.7113 | 239.8346 | 239.8346 | 239.8346 | 239.8346 | 239.8346 | 239.8346 | 239.8346
Weighted Cost of EUSE |  | 48775340.0903 | 17073.4658 | 252374.0468 | 2014702.3174 | 1714592.774 | 2614975.7385 | 4339316.8934 | 5460168.4993 | 8625974.3459 | 9459077.8359 | 9459077.8359 | 9459077.8359 | 9459077.8359 | 9459077.8359 | 9459077.8359 | 9459077.8359
Benefits |  | 217502411.1222 | 0 | 0 | -876998.2679 | 380782.8697 | 2435093.4107 | 7368639.0108 | 14766538.2798 | 29929778.4218 | 54497849.8423 | 54497849.8423 | 54497849.8423 | 54497849.8423 | 54497849.8423 | 54497849.8423 | 54497849.8423
Costs |  | 7850646.3158 | 0 | 7711377.375 | 118562.4271 | 121526.4878 | 124564.65 | 127678.7663 | 130870.7354 | 134142.5038 | 137496.0664 | 140933.4681 | 144456.8048 | 148068.2249 | 151769.9305 | 155564.1788 | 159453.2832
Net Economic Benefit |  | 209651764.8064
Option 4
Weighted EUSE (MWh) |  |  | 0.4329 | 6.3989 | 0 | 0 | 0 | 0 | 0.00050914 | 0.0042025 | 0.025804 | 0.025804 | 0.025804 | 0.025804 | 0.025804 | 0.025804 | 0.025804
Weighted Cost of EUSE |  | 242638.654 | 17073.4658 | 252374.0468 | 0 | 0 | 0 | 0 | 20.0804 | 165.7453 | 1017.7041 | 1017.7041 | 1017.7041 | 1017.7041 | 1017.7041 | 1017.7041 | 1017.7041
Benefits |  | 266035112.5585 | 0 | 0 | 1137704.0495 | 2095375.6437 | 5050069.1492 | 11707955.9042 | 20226686.6986 | 38555587.0224 | 63955909.974 | 63955909.974 | 63955909.974 | 63955909.974 | 63955909.974 | 63955909.974 | 63955909.974
Costs |  | 14504089.9256 | 0 | 14246790.1875 | 219044.3991 | 224520.5091 | 230133.5218 | 235886.8599 | 241784.0314 | 247828.6322 | 254024.348 | 260374.9567 | 266884.3306 | 273556.4389 | 280395.3498 | 287405.2336 | 294590.3644
Net Economic Benefit |  | 251531022.6329

## Cost-Benefit (cost-30%)
VCR | 39440 |  | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
Discount Rate | 6.37%
Cost Sensitivity | 0.7
Do Nothing
Weighted EUSE (MWh) |  |  | 0.4329 | 6.3989 | 28.8465 | 53.1282 | 128.0443 | 296.8549 | 512.8475 | 977.5799 | 1621.626 | 1621.626 | 1621.626 | 1621.626 | 1621.626 | 1621.626 | 1621.626
Weighted Cost of EUSE |  | 266277751.2125 | 17073.4658 | 252374.0468 | 1137704.0495 | 2095375.6437 | 5050069.1492 | 11707955.9042 | 20226706.779 | 38555752.7677 | 63956927.6781 | 63956927.6781 | 63956927.6781 | 63956927.6781 | 63956927.6781 | 63956927.6781 | 63956927.6781
Benefits |  | -266277751.2125 | -17073.4658 | -252374.0468 | -1137704.0495 | -2095375.6437 | -5050069.1492 | -11707955.9042 | -20226706.779 | -38555752.7677 | -63956927.6781 | -63956927.6781 | -63956927.6781 | -63956927.6781 | -63956927.6781 | -63956927.6781 | -63956927.6781
Costs |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Net Economic Benefit |  | -266277751.2125
Option 1
Weighted EUSE (MWh) |  |  | 0.4329 | 6.3989 | 0.00018346 | 0.00072561 | 0.0035361 | 0.013887 | 0.030374 | 3.2231 | 10.0316 | 10.0316 | 10.0316 | 10.0316 | 10.0316 | 10.0316 | 10.0316
Weighted Cost of EUSE |  | 1648054.169 | 17073.4658 | 252374.0468 | 7.2355 | 28.618 | 139.4619 | 547.7109 | 1197.9528 | 127120.9211 | 395648.0728 | 395648.0728 | 395648.0728 | 395648.0728 | 395648.0728 | 395648.0728 | 395648.0728
Benefits |  | 264629697.0434 | 0 | 0 | 1137696.814 | 2095347.0258 | 5049929.6873 | 11707408.1934 | 20225508.8263 | 38428631.8466 | 63561279.6053 | 63561279.6053 | 63561279.6053 | 63561279.6053 | 63561279.6053 | 63561279.6053 | 63561279.6053
Costs |  | 9796247.7829 | 0 | 9622464.25 | 147945.3878 | 151644.0225 | 155435.1231 | 159321.0012 | 163304.0262 | 167386.6269 | 171571.2925 | 175860.5749 | 180257.0892 | 184763.5165 | 189382.6044 | 194117.1695 | 198970.0987
Net Economic Benefit |  | 254833449.2605
Option 2
Weighted EUSE (MWh) |  |  | 0.4329 | 6.3989 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 0.00034 | 0.00034
Weighted Cost of EUSE |  | 239148.226 | 17073.4658 | 252374.0468 | 0 | 0 | 0 | 0 | 0 | 0 | 13.4096 | 13.4096 | 13.4096 | 13.4096 | 13.4096 | 13.4096 | 13.4096
Benefits |  | 266038602.9865 | 0 | 0 | 1137704.0495 | 2095375.6437 | 5050069.1492 | 11707955.9042 | 20226706.779 | 38555752.7677 | 63956914.2685 | 63956914.2685 | 63956914.2685 | 63956914.2685 | 63956914.2685 | 63956914.2685 | 63956914.2685
Costs |  | 11512314.0536 | 0 | 11308087 | 173861.8376 | 178208.3836 | 182663.5932 | 187230.183 | 191910.9376 | 196708.711 | 201626.4288 | 206667.0895 | 211833.7667 | 217129.6109 | 222557.8512 | 228122.4974 | 233826.2531
Net Economic Benefit |  | 254526288.9329
Option 3
Weighted EUSE (MWh) |  |  | 0.4329 | 6.3989 | 51.0827 | 43.4734 | 66.3026 | 110.0232 | 138.4424 | 218.7113 | 239.8346 | 239.8346 | 239.8346 | 239.8346 | 239.8346 | 239.8346 | 239.8346
Weighted Cost of EUSE |  | 48775340.0903 | 17073.4658 | 252374.0468 | 2014702.3174 | 1714592.774 | 2614975.7385 | 4339316.8934 | 5460168.4993 | 8625974.3459 | 9459077.8359 | 9459077.8359 | 9459077.8359 | 9459077.8359 | 9459077.8359 | 9459077.8359 | 9459077.8359
Benefits |  | 217502411.1222 | 0 | 0 | -876998.2679 | 380782.8697 | 2435093.4107 | 7368639.0108 | 14766538.2798 | 29929778.4218 | 54497849.8423 | 54497849.8423 | 54497849.8423 | 54497849.8423 | 54497849.8423 | 54497849.8423 | 54497849.8423
Costs |  | 4227271.0931 | 0 | 4152280.125 | 63841.3069 | 65437.3396 | 67073.2731 | 68750.1049 | 70468.8575 | 72230.579 | 74036.3434 | 75887.252 | 77784.4333 | 79729.0442 | 81722.2703 | 83765.327 | 85859.4602
Net Economic Benefit |  | 213275140.0291
Option 4
Weighted EUSE (MWh) |  |  | 0.4329 | 6.3989 | 0 | 0 | 0 | 0 | 0.00050914 | 0.0042025 | 0.025804 | 0.025804 | 0.025804 | 0.025804 | 0.025804 | 0.025804 | 0.025804
Weighted Cost of EUSE |  | 242638.654 | 17073.4658 | 252374.0468 | 0 | 0 | 0 | 0 | 20.0804 | 165.7453 | 1017.7041 | 1017.7041 | 1017.7041 | 1017.7041 | 1017.7041 | 1017.7041 | 1017.7041
Benefits |  | 266035112.5585 | 0 | 0 | 1137704.0495 | 2095375.6437 | 5050069.1492 | 11707955.9042 | 20226686.6986 | 38555587.0224 | 63955909.974 | 63955909.974 | 63955909.974 | 63955909.974 | 63955909.974 | 63955909.974 | 63955909.974
Costs |  | 7809894.5753 | 0 | 7671348.5625 | 117946.9841 | 120895.6588 | 123918.0502 | 127016.0015 | 130191.4015 | 133446.1866 | 136782.3412 | 140201.8997 | 143706.9472 | 147299.6209 | 150982.1114 | 154756.6642 | 158625.5808
Net Economic Benefit |  | 258225217.9832