## Report summary Table
Table 8-2: Market benefits of augmentation options relative to the base case
Augmentation option | Total lifecycle project cost (2017-2032) ($M, real 2017) | NPV of net economic benefit (2017-2032 ) $M | Project ranking
Base Case - Do Nothing |  |  | N/A
Option 1 - Reconductor the 66kV loop with higher capacity conductor in 2019 | 13.084 | 6.0685 | 2
Option 2 - Install a new KTS-MAT 66kV line to form a four legged 66kV loop in 2019 | 15.376 | 3.6173 | 3
Option 3 - Split the existing 66kV loop by installing one additional 66kV line in 2019 | 5.646 | -34.1574 | 4
Option 4 - Split the existing 66kV loop by installing two additional 66kV lines in 2019 | 10.431 | 8.9065 | 1

## Sensitivity Analysis Summary
Option | Net Economic Benefit ($) | Rank | Net Economic Benefit ($) | Rank | Net Economic Benefit ($) | Rank | Net Economic Benefit ($) | Rank | Net Economic Benefit ($) | Rank | Net Economic Benefit ($) | Rank | Average Net Economic benefit ($) | Overall Rank of Feasible Options | Include Option in Ranking?
| Base (planning) scenario |  | VCR High (+20%) |  | VCR Low (-20%) |  | Discount Rate High (8.26%) |  | Investment Cost High (+30%) |  | Investment Cost Low (-30%)
Option 1 | 6068492.4589 | 2 | 10082807.878 | 2 | 2056992.022 | 2 | 3105129.5514 | 2 | 1871508.0431 | 2 | 10268291.857 | 2 | 5575536.9684 | 2 | yes
Option 2 | 3617340.2534 | 3 | 7631729.8802 | 3 | -394234.3911 | 3 | 771840.0925 | 3 | -1315101.1356 | 3 | 8552596.6246 | 3 | 3144028.554 | 3 | yes
Option 3 | -34157368.7788 | 4 | -39779361.8044 | 4 | -28532560.7711 | 4 | -29775283.6421 | 4 | -35967648.8991 | 4 | -32344273.6764 | 4 | -33426082.9287 | 4 | yes
Option 4 | 8906510.9367 | 1 | 12920900.5635 | 1 | 4894936.2922 | 1 | 5806578.4075 | 1 | 5560820.7527 | 1 | 12255016.1029 | 1 | 8390793.8426 | 1 | yes

## Opt 3 - Economic timing
Discount Rate | 6.37%
PV cost (Capital and Operational) $ | 6038958.7044
Year | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
Base case ( Do nothing) EUSE | 771.6803 | 771.6803 | 14585.661 | 123838.7413 | 140524.8932 | 376738.0117 | 872697.1506 | 1572932.778 | 4105878.2237 | 5634952.985 | 5634952.985 | 5634952.985 | 5634952.985 | 5634952.985 | 5634952.985
Annualised benefits after implementation of Option 3 ($) | -771.6803 | -771.6803 | 14585.661 | 123838.7413 | 140524.8932 | 376738.0117 | 872697.1506 | 1572932.778 | 4105878.2237 | 5634952.985 | 5634952.985 | 5634952.985 | 5634952.985 | 5634952.985 | 5634952.985
Annualised benefits after implementation of Option 3 ($M) - planning | -0.00077168 | -0.00077168 | 0.014586 | 0.12384 | 0.14052 | 0.37674 | 0.8727 | 1.5729 | 4.1059 | 5.635 | 5.635 | 5.635 | 5.635 | 5.635 | 5.635
Annualised cost for Option 3 ($) | 403064.6864 | 403064.6864 | 403064.6864 | 403064.6864 | 403064.6864 | 403064.6864 | 403064.6864 | 403064.6864 | 403064.6864 | 403064.6864 | 403064.6864 | 403064.6864 | 403064.6864 | 403064.6864 | 403064.6864
Annualised cost for Option 3 ($M) | 0.40306 | 0.40306 | 0.40306 | 0.40306 | 0.40306 | 0.40306 | 0.40306 | 0.40306 | 0.40306 | 0.40306 | 0.40306 | 0.40306 | 0.40306 | 0.40306 | 0.40306
moderate | -0.017073 | -0.25237 | 1.1377 | 2.0954 | 5.0501 | 11.708 | 20.2267 | 38.5558 | 63.9569 | 63.9569 | 63.9569 | 63.9569 | 63.9569 | 63.9569 | 63.9569
fast | -0.30025 | -2.4146 | 10.5093 | 21.6351 | 26.0866 | 33.7868 | 38.634 | 52.443 | 63.9569 | 63.9569 | 63.9569 | 63.9569 | 63.9569 | 63.9569 | 63.9569

## Option Costs
Year |  | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
Discount Rate | 6.37%
Inflation Rate | 2.5%
O&M cost | 1.5%
Option 1 |  | 0 | 13746377.5 | 211350.5541 | 216634.3179 | 222050.1759 | 227601.4303 | 233291.466 | 239123.7527 | 245101.8465 | 251229.3926 | 257510.1275 | 263947.8806 | 270546.5777 | 277310.2421 | 284242.9982
Capital |  | 0 | 13746377.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Operational |  | 0 | 0 | 211350.5541 | 216634.3179 | 222050.1759 | 227601.4303 | 233291.466 | 239123.7527 | 245101.8465 | 251229.3926 | 257510.1275 | 263947.8806 | 270546.5777 | 277310.2421 | 284242.9982
Option 2 |  | 0 | 16154410 | 248374.0537 | 254583.4051 | 260947.9902 | 267471.69 | 274158.4822 | 281012.4443 | 288037.7554 | 295238.6993 | 302619.6668 | 310185.1584 | 317939.7874 | 325889.2821 | 334037.5045
Capital |  | 0 | 16154410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2
Operational |  | 0 | 0 | 248374.0537 | 254583.4051 | 260947.9902 | 267471.69 | 274158.4822 | 281012.4443 | 288037.7554 | 295238.6993 | 302619.6668 | 310185.1584 | 317939.7874 | 325888.2821 | 334035.5045
Option 3 |  | 0 | 5931828.75 | 91201.867 | 93481.9137 | 95818.9615 | 98214.4356 | 100669.7965 | 103186.5414 | 105766.2049 | 108410.36 | 111120.619 | 113898.6345 | 116746.1004 | 119664.7529 | 122656.3717
Capital |  | 0 | 5931828.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Operational |  | 0 | 0 | 91201.867 | 93481.9137 | 95818.9615 | 98214.4356 | 100669.7965 | 103186.5414 | 105766.2049 | 108410.36 | 111120.619 | 113898.6345 | 116746.1004 | 119664.7529 | 122656.3717
Option 4 |  | 0 | 10959069.375 | 168495.6916 | 172708.0839 | 177025.786 | 181451.4307 | 185987.7164 | 190637.4094 | 195403.3446 | 200288.4282 | 205295.6389 | 210428.0299 | 215688.7306 | 221080.9489 | 226607.9726
Capital |  | 0 | 10959069.375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Operational |  | 0 | 0 | 168495.6916 | 172708.0839 | 177025.786 | 181451.4307 | 185987.7164 | 190637.4094 | 195403.3446 | 200288.4282 | 205295.6389 | 210428.0299 | 215688.7306 | 221080.9489 | 226607.9726
| Real $2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
Option 1 - Reconductor the 66kV loop with higher capacity conductor in 2019 | 13084000 | 13411100 | 13746377.5 | 14090036.9375 | 14442287.8609 | 14803345.0575 | 15173428.6839 | 15552764.401 | 15941583.511 | 16340123.0988 | 16748626.1763 | 17167341.8307 | 17596525.3764 | 18036438.5108 | 18487349.4736 | 18949533.2105
Option 2 - Install a new KTS-MAT 66kV line to form a four legged 66kV loop in 2019 | 15376000 | 15760400 | 16154410 | 16558270.25 | 16972227.0062 | 17396532.6814 | 17831445.9984 | 18277232.1484 | 18734162.9521 | 19202517.0259 | 19682579.9516 | 20174644.4504 | 20679010.5616 | 21195985.8257 | 21725885.4713 | 22269032.6081
Option 3 - Split the existing 66kV loop by installing one additional 66kV line in 2019 | 5646000 | 5787150 | 5931828.75 | 6080124.4687 | 6232127.5805 | 6387930.77 | 6547629.0392 | 6711319.7652 | 6879102.7593 | 7051080.3283 | 7227357.3365 | 7408041.2699 | 7593242.3017 | 7783073.3592 | 7977650.1932 | 8177091.448
Option 4 - Split the existing 66kV loop by installing two additional 66kV lines in 2019 | 10431000 | 10691775 | 10959069.375 | 11233046.1094 | 11513872.2621 | 11801719.0687 | 12096762.0454 | 12399181.0965 | 12709160.6239 | 13026889.6395 | 13352561.8805 | 13686375.9275 | 14028535.3257 | 14379248.7089 | 14738729.9266 | 15107198.1747

## Cost-Benefit (BASE)
VCR | 39440 |  | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
Discount Rate | 6.37%
Option costs | $2017 Real
Do Nothing
Weighted EUSE (MWh) |  |  | 0.019566 | 0.019566 | 0.36982 | 3.1399 | 3.563 | 9.5522 | 22.1272 | 39.8817 | 104.1044 | 142.8741 | 142.8741 | 142.8741 | 142.8741 | 142.8741 | 142.8741
Weighted Cost of EUSE |  |  | 771.6803 | 771.6803 | 14585.661 | 123838.7413 | 140524.8932 | 376738.0117 | 872697.1506 | 1572932.778 | 4105878.2237 | 5634952.985 | 5634952.985 | 5634952.985 | 5634952.985 | 5634952.985 | 5634952.985
Benefits |  | -20066318.1693 | -771.6803 | -771.6803 | -14585.661 | -123838.7413 | -140524.8932 | -376738.0117 | -872697.1506 | -1572932.778 | -4105878.2237 | -5634952.985 | -5634952.985 | -5634952.985 | -5634952.985 | -5634952.985 | -5634952.985
Costs |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Net Economic Benefit |  | -20066318.1693
Option 1
Weighted EUSE (MWh) |  |  | 0.019566 | 0.019566 | 0 | 0 | 0 | 4.9859e-05 | 0.00055085 | 0.0012561 | 0.0024538 | 0.0024538 | 0.0024538 | 0.0024538 | 0.0024538 | 0.0024538 | 0.0024538
Weighted Cost of EUSE |  | 1778.5295 | 771.6803 | 771.6803 | 0 | 0 | 0 | 1.9664 | 21.7256 | 49.5389 | 96.7788 | 96.7788 | 96.7788 | 96.7788 | 96.7788 | 96.7788 | 96.7788
Benefits |  | 20063132.1488 | -771.6803 | -771.6803 | 14585.661 | 123838.7413 | 140524.8932 | 376736.0452 | 872675.425 | 1572883.2391 | 4105781.4449 | 5634856.2062 | 5634856.2062 | 5634856.2062 | 5634856.2062 | 5634856.2062 | 5634856.2062
Costs |  | 13994639.6898 | 0 | 13746377.5 | 211350.5541 | 216634.3179 | 222050.1759 | 227601.4303 | 233291.466 | 239123.7527 | 245101.8465 | 251229.3926 | 257510.1275 | 263947.8806 | 270546.5777 | 277310.2421 | 284242.9982
Net Economic Benefit |  | 6068492.4589
Option 2
Weighted EUSE (MWh) |  |  | 0.019566 | 0.019566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Cost of EUSE |  | 1407.4911 | 771.6803 | 771.6803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Benefits |  | 20063503.1872 | -771.6803 | -771.6803 | 14585.661 | 123838.7413 | 140524.8932 | 376738.0117 | 872697.1506 | 1572932.778 | 4105878.2237 | 5634952.985 | 5634952.985 | 5634952.985 | 5634952.985 | 5634952.985 | 5634952.985
Costs |  | 16446162.9337 | 0 | 16154410 | 248374.0537 | 254583.4051 | 260947.9902 | 267471.69 | 274158.4822 | 281012.4443 | 288037.7554 | 295238.6993 | 302619.6668 | 310185.1584 | 317939.7874 | 325889.2821 | 334037.5045
Net Economic Benefit |  | 3617340.2534
Option 3
Weighted EUSE (MWh) |  |  | 0.019566 | 0.019566 | 47.2391 | 37.5363 | 61.7954 | 97.4041 | 121.4564 | 211.62 | 247.6341 | 247.6341 | 247.6341 | 247.6341 | 247.6341 | 247.6341 | 247.6341
Weighted Cost of EUSE |  | 48183320.7527 | 771.6803 | 771.6803 | 1863108.9243 | 1480432.2606 | 2437210.4809 | 3841617.7273 | 4790239.8771 | 8346293.5257 | 9766690.6328 | 9766690.6328 | 9766690.6328 | 9766690.6328 | 9766690.6328 | 9766690.6328 | 9766690.6328
Benefits |  | -28118410.0744 | -771.6803 | -771.6803 | -1848523.2633 | -1356593.5193 | -2296685.5877 | -3464879.7156 | -3917542.7265 | -6773360.7477 | -5660812.4091 | -4131737.6478 | -4131737.6478 | -4131737.6478 | -4131737.6478 | -4131737.6478 | -4131737.6478
Costs |  | 6038958.7044 | 0 | 5931828.75 | 91201.867 | 93481.9137 | 95818.9615 | 98214.4356 | 100669.7965 | 103186.5414 | 105766.2049 | 108410.36 | 111120.619 | 113898.6345 | 116746.1004 | 119664.7529 | 122656.3717
Net Economic Benefit |  | -34157368.7788
Option 4
Weighted EUSE (MWh) |  |  | 0.019566 | 0.019566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Cost of EUSE |  | 1407.4911 | 771.6803 | 771.6803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Benefits |  | 20063503.1872 | -771.6803 | -771.6803 | 14585.661 | 123838.7413 | 140524.8932 | 376738.0117 | 872697.1506 | 1572932.778 | 4105878.2237 | 5634952.985 | 5634952.985 | 5634952.985 | 5634952.985 | 5634952.985 | 5634952.985
Costs |  | 11156992.2504 | 0 | 10959069.375 | 168495.6916 | 172708.0839 | 177025.786 | 181451.4307 | 185987.7164 | 190637.4094 | 195403.3446 | 200288.4282 | 205295.6389 | 210428.0299 | 215688.7306 | 221080.9489 | 226607.9726
Net Economic Benefit |  | 8906510.9367
Note: Option 4 addresses KTS-TMA-MAT EUSE but AW-PV becomes two legged loop making things worse during KTS-AW outage. Hence the NPV is -ve for this option
|  |  | 0.019566 | 0.019566 | 47.2391 | 37.5363 | 61.7954 | 97.4041 | 121.4564 | 211.62 | 247.6341 | 247.6341 | 247.6341 | 247.6341 | 247.6341 | 247.6341 | 247.6341

## Cost-Benefit (VCR+20%)
VCR | 47328 |  | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
Discount Rate | 6.37%
Option costs | $2017 Real
Do Nothing
Weighted EUSE (MWh) |  |  | 0.019566 | 0.019566 | 0.36982 | 3.1399 | 3.563 | 9.5522 | 22.1272 | 39.8817 | 104.1044 | 142.8741 | 142.8741 | 142.8741 | 142.8741 | 142.8741 | 142.8741
Weighted Cost of EUSE |  | 24079581.8032 | 926.0163 | 926.0163 | 17502.7932 | 148606.4896 | 168629.8719 | 452085.614 | 1047236.5807 | 1887519.3336 | 4927053.8684 | 6761943.582 | 6761943.582 | 6761943.582 | 6761943.582 | 6761943.582 | 6761943.582
Benefits |  | -24079581.8032 | -926.0163 | -926.0163 | -17502.7932 | -148606.4896 | -168629.8719 | -452085.614 | -1047236.5807 | -1887519.3336 | -4927053.8684 | -6761943.582 | -6761943.582 | -6761943.582 | -6761943.582 | -6761943.582 | -6761943.582
Costs |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Net Economic Benefit |  | -24079581.8032
Option 1
Weighted EUSE (MWh) |  |  | 0.019566 | 0.019566 | 0 | 0 | 0 | 4.9859e-05 | 0.00055085 | 0.0012561 | 0.0024538 | 0.0024538 | 0.0024538 | 0.0024538 | 0.0024538 | 0.0024538 | 0.0024538
Weighted Cost of EUSE |  | 2134.2354 | 926.0163 | 926.0163 | 0 | 0 | 0 | 2.3597 | 26.0707 | 59.4467 | 116.1345 | 116.1345 | 116.1345 | 116.1345 | 116.1345 | 116.1345 | 116.1345
Benefits |  | 24077447.5678 | 0 | 0 | 17502.7932 | 148606.4896 | 168629.8719 | 452083.2543 | 1047210.5101 | 1887459.887 | 4926937.7339 | 6761827.4475 | 6761827.4475 | 6761827.4475 | 6761827.4475 | 6761827.4475 | 6761827.4475
Costs |  | 13994639.6898 | 0 | 13746377.5 | 211350.5541 | 216634.3179 | 222050.1759 | 227601.4303 | 233291.466 | 239123.7527 | 245101.8465 | 251229.3926 | 257510.1275 | 263947.8806 | 270546.5777 | 277310.2421 | 284242.9982
Net Economic Benefit |  | 10082807.878
Option 2
Weighted EUSE (MWh) |  |  | 0.019566 | 0.019566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Cost of EUSE |  | 1688.9893 | 926.0163 | 926.0163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Benefits |  | 24077892.8139 | 0 | 0 | 17502.7932 | 148606.4896 | 168629.8719 | 452085.614 | 1047236.5807 | 1887519.3336 | 4927053.8684 | 6761943.582 | 6761943.582 | 6761943.582 | 6761943.582 | 6761943.582 | 6761943.582
Costs |  | 16446162.9337 | 0 | 16154410 | 248374.0537 | 254583.4051 | 260947.9902 | 267471.69 | 274158.4822 | 281012.4443 | 288037.7554 | 295238.6993 | 302619.6668 | 310185.1584 | 317939.7874 | 325889.2821 | 334037.5045
Net Economic Benefit |  | 7631729.8802
Option 3
Weighted EUSE (MWh) |  |  | 0.019566 | 0.019566 | 47.2391 | 37.5363 | 61.7954 | 97.4041 | 121.4564 | 211.62 | 247.6341 | 247.6341 | 247.6341 | 247.6341 | 247.6341 | 247.6341 | 247.6341
Weighted Cost of EUSE |  | 57819984.9032 | 926.0163 | 926.0163 | 2235730.7092 | 1776518.7127 | 2924652.5771 | 4609941.2728 | 5748287.8526 | 10015552.2308 | 11720028.7593 | 11720028.7593 | 11720028.7593 | 11720028.7593 | 11720028.7593 | 11720028.7593 | 11720028.7593
Benefits |  | -33740403.1 | 0 | 0 | -2218227.916 | -1627912.2231 | -2756022.7053 | -4157855.6588 | -4701051.2718 | -8128032.8972 | -6792974.8909 | -4958085.1773 | -4958085.1773 | -4958085.1773 | -4958085.1773 | -4958085.1773 | -4958085.1773
Costs |  | 6038958.7044 | 0 | 5931828.75 | 91201.867 | 93481.9137 | 95818.9615 | 98214.4356 | 100669.7965 | 103186.5414 | 105766.2049 | 108410.36 | 111120.619 | 113898.6345 | 116746.1004 | 119664.7529 | 122656.3717
Net Economic Benefit |  | -39779361.8044
Option 4
Weighted EUSE (MWh) |  |  | 0.019566 | 0.019566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Cost of EUSE |  | 1688.9893 | 926.0163 | 926.0163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Benefits |  | 24077892.8139 | 0 | 0 | 17502.7932 | 148606.4896 | 168629.8719 | 452085.614 | 1047236.5807 | 1887519.3336 | 4927053.8684 | 6761943.582 | 6761943.582 | 6761943.582 | 6761943.582 | 6761943.582 | 6761943.582
Costs |  | 11156992.2504 | 0 | 10959069.375 | 168495.6916 | 172708.0839 | 177025.786 | 181451.4307 | 185987.7164 | 190637.4094 | 195403.3446 | 200288.4282 | 205295.6389 | 210428.0299 | 215688.7306 | 221080.9489 | 226607.9726
Net Economic Benefit |  | 12920900.5635

## Cost-Benefit (VCR-20%)
VCR | 31552 |  | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
Discount Rate | 6.37%
Option costs | $2017 Real
Do Nothing
Weighted EUSE (MWh) |  |  | 0.019566 | 0.019566 | 0.36982 | 3.1399 | 3.563 | 9.5522 | 22.1272 | 39.8817 | 104.1044 | 142.8741 | 142.8741 | 142.8741 | 142.8741 | 142.8741 | 142.8741
Weighted Cost of EUSE |  | 16053054.5355 | 617.3442 | 617.3442 | 11668.5288 | 99070.9931 | 112419.9146 | 301390.4093 | 698157.7205 | 1258346.2224 | 3284702.5789 | 4507962.388 | 4507962.388 | 4507962.388 | 4507962.388 | 4507962.388 | 4507962.388
Benefits |  | -16053054.5355 | -617.3442 | -617.3442 | -11668.5288 | -99070.9931 | -112419.9146 | -301390.4093 | -698157.7205 | -1258346.2224 | -3284702.5789 | -4507962.388 | -4507962.388 | -4507962.388 | -4507962.388 | -4507962.388 | -4507962.388
Costs |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Net Economic Benefit |  | -16053054.5355
Option 1
Weighted EUSE (MWh) |  |  | 0.019566 | 0.019566 | 0 | 0 | 0 | 4.9859e-05 | 0.00055085 | 0.0012561 | 0.0024538 | 0.0024538 | 0.0024538 | 0.0024538 | 0.0024538 | 0.0024538 | 0.0024538
Weighted Cost of EUSE |  | 1422.8236 | 617.3442 | 617.3442 | 0 | 0 | 0 | 1.5731 | 17.3805 | 39.6311 | 77.423 | 77.423 | 77.423 | 77.423 | 77.423 | 77.423 | 77.423
Benefits |  | 16051631.7119 | 0 | 0 | 11668.5288 | 99070.9931 | 112419.9146 | 301388.8362 | 698140.34 | 1258306.5913 | 3284625.1559 | 4507884.965 | 4507884.965 | 4507884.965 | 4507884.965 | 4507884.965 | 4507884.965
Costs |  | 13994639.6898 | 0 | 13746377.5 | 211350.5541 | 216634.3179 | 222050.1759 | 227601.4303 | 233291.466 | 239123.7527 | 245101.8465 | 251229.3926 | 257510.1275 | 263947.8806 | 270546.5777 | 277310.2421 | 284242.9982
Net Economic Benefit |  | 2056992.022
Option 2
Weighted EUSE (MWh) |  |  | 0.019566 | 0.019566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Cost of EUSE |  | 1125.9929 | 617.3442 | 617.3442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Benefits |  | 16051928.5426 | 0 | 0 | 11668.5288 | 99070.9931 | 112419.9146 | 301390.4093 | 698157.7205 | 1258346.2224 | 3284702.5789 | 4507962.388 | 4507962.388 | 4507962.388 | 4507962.388 | 4507962.388 | 4507962.388
Costs |  | 16446162.9337 | 0 | 16154410 | 248374.0537 | 254583.4051 | 260947.9902 | 267471.69 | 274158.4822 | 281012.4443 | 288037.7554 | 295238.6993 | 302619.6668 | 310185.1584 | 317939.7874 | 325889.2821 | 334037.5045
Net Economic Benefit |  | -394234.3911
Option 3
Weighted EUSE (MWh) |  |  | 0.019566 | 0.019566 | 47.2391 | 37.5363 | 61.7954 | 97.4041 | 121.4564 | 211.62 | 247.6341 | 247.6341 | 247.6341 | 247.6341 | 247.6341 | 247.6341 | 247.6341
Weighted Cost of EUSE |  | 38546656.6021 | 617.3442 | 617.3442 | 1490487.1394 | 1184345.8085 | 1949768.3848 | 3073294.1819 | 3832191.9017 | 6677034.8205 | 7813352.5062 | 7813352.5062 | 7813352.5062 | 7813352.5062 | 7813352.5062 | 7813352.5062 | 7813352.5062
Benefits |  | -22493602.0667 | 0 | 0 | -1478818.6107 | -1085274.8154 | -1837348.4702 | -2771903.7725 | -3134034.1812 | -5418688.5981 | -4528649.9273 | -3305390.1182 | -3305390.1182 | -3305390.1182 | -3305390.1182 | -3305390.1182 | -3305390.1182
Costs |  | 6038958.7044 | 0 | 5931828.75 | 91201.867 | 93481.9137 | 95818.9615 | 98214.4356 | 100669.7965 | 103186.5414 | 105766.2049 | 108410.36 | 111120.619 | 113898.6345 | 116746.1004 | 119664.7529 | 122656.3717
Net Economic Benefit |  | -28532560.7711
Option 4
Weighted EUSE (MWh) |  |  | 0.019566 | 0.019566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Cost of EUSE |  | 1125.9929 | 617.3442 | 617.3442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Benefits |  | 16051928.5426 | 0 | 0 | 11668.5288 | 99070.9931 | 112419.9146 | 301390.4093 | 698157.7205 | 1258346.2224 | 3284702.5789 | 4507962.388 | 4507962.388 | 4507962.388 | 4507962.388 | 4507962.388 | 4507962.388
Costs |  | 11156992.2504 | 0 | 10959069.375 | 168495.6916 | 172708.0839 | 177025.786 | 181451.4307 | 185987.7164 | 190637.4094 | 195403.3446 | 200288.4282 | 205295.6389 | 210428.0299 | 215688.7306 | 221080.9489 | 226607.9726
Net Economic Benefit |  | 4894936.2922

## Cost-Benefit (Disc rate high)
VCR | 39440 |  | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
Discount Rate | 8.26%
Option costs | $2017 Real
Do Nothing
Weighted EUSE (MWh) |  |  | 0.019566 | 0.019566 | 0.36982 | 3.1399 | 3.563 | 9.5522 | 22.1272 | 39.8817 | 104.1044 | 142.8741 | 142.8741 | 142.8741 | 142.8741 | 142.8741 | 142.8741
Weighted Cost of EUSE |  | 16428241.9509 | 771.6803 | 771.6803 | 14585.661 | 123838.7413 | 140524.8932 | 376738.0117 | 872697.1506 | 1572932.778 | 4105878.2237 | 5634952.985 | 5634952.985 | 5634952.985 | 5634952.985 | 5634952.985 | 5634952.985
Benefits |  | -16428241.9509 | -771.6803 | -771.6803 | -14585.661 | -123838.7413 | -140524.8932 | -376738.0117 | -872697.1506 | -1572932.778 | -4105878.2237 | -5634952.985 | -5634952.985 | -5634952.985 | -5634952.985 | -5634952.985 | -5634952.985
Costs |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Net Economic Benefit |  | -16428241.9509
Option 1
Weighted EUSE (MWh) |  |  | 0.019566 | 0.019566 | 0 | 0 | 0 | 4.9859e-05 | 0.00055085 | 0.0012561 | 0.0024538 | 0.0024538 | 0.0024538 | 0.0024538 | 0.0024538 | 0.0024538 | 0.0024538
Weighted Cost of EUSE |  | 1675.8397 | 771.6803 | 771.6803 | 0 | 0 | 0 | 1.9664 | 21.7256 | 49.5389 | 96.7788 | 96.7788 | 96.7788 | 96.7788 | 96.7788 | 96.7788 | 96.7788
Benefits |  | 16426566.1111 | 0 | 0 | 14585.661 | 123838.7413 | 140524.8932 | 376736.0452 | 872675.425 | 1572883.2391 | 4105781.4449 | 5634856.2062 | 5634856.2062 | 5634856.2062 | 5634856.2062 | 5634856.2062 | 5634856.2062
Costs |  | 13321436.5598 | 0 | 13746377.5 | 211350.5541 | 216634.3179 | 222050.1759 | 227601.4303 | 233291.466 | 239123.7527 | 245101.8465 | 251229.3926 | 257510.1275 | 263947.8806 | 270546.5777 | 277310.2421 | 284242.9982
Net Economic Benefit |  | 3105129.5514
Option 2
Weighted EUSE (MWh) |  |  | 0.019566 | 0.019566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Cost of EUSE |  | 1371.2203 | 771.6803 | 771.6803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Benefits |  | 16426870.7306 | 0 | 0 | 14585.661 | 123838.7413 | 140524.8932 | 376738.0117 | 872697.1506 | 1572932.778 | 4105878.2237 | 5634952.985 | 5634952.985 | 5634952.985 | 5634952.985 | 5634952.985 | 5634952.985
Costs |  | 15655030.6381 | 0 | 16154410 | 248374.0537 | 254583.4051 | 260947.9902 | 267471.69 | 274158.4822 | 281012.4443 | 288037.7554 | 295238.6993 | 302619.6668 | 310185.1584 | 317939.7874 | 325889.2821 | 334037.5045
Net Economic Benefit |  | 771840.0925
Option 3
Weighted EUSE (MWh) |  |  | 0.019566 | 0.019566 | 47.2391 | 37.5363 | 61.7954 | 97.4041 | 121.4564 | 211.62 | 247.6341 | 247.6341 | 247.6341 | 247.6341 | 247.6341 | 247.6341 | 247.6341
Weighted Cost of EUSE |  | 40455067.108 | 771.6803 | 771.6803 | 1863108.9243 | 1480432.2606 | 2437210.4809 | 3841617.7273 | 4790239.8771 | 8346293.5257 | 9766690.6328 | 9766690.6328 | 9766690.6328 | 9766690.6328 | 9766690.6328 | 9766690.6328 | 9766690.6328
Benefits |  | -24026825.1571 | 0 | 0 | -1848523.2633 | -1356593.5193 | -2296685.5877 | -3464879.7156 | -3917542.7265 | -6773360.7477 | -5660812.4091 | -4131737.6478 | -4131737.6478 | -4131737.6478 | -4131737.6478 | -4131737.6478 | -4131737.6478
Costs |  | 5748458.4849 | 0 | 5931828.75 | 91201.867 | 93481.9137 | 95818.9615 | 98214.4356 | 100669.7965 | 103186.5414 | 105766.2049 | 108410.36 | 111120.619 | 113898.6345 | 116746.1004 | 119664.7529 | 122656.3717
Net Economic Benefit |  | -29775283.6421
Option 4
Weighted EUSE (MWh) |  |  | 0.019566 | 0.019566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Cost of EUSE |  | 1371.2203 | 771.6803 | 771.6803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Benefits |  | 16426870.7306 | 0 | 0 | 14585.661 | 123838.7413 | 140524.8932 | 376738.0117 | 872697.1506 | 1572932.778 | 4105878.2237 | 5634952.985 | 5634952.985 | 5634952.985 | 5634952.985 | 5634952.985 | 5634952.985
Costs |  | 10620292.3231 | 0 | 10959069.375 | 168495.6916 | 172708.0839 | 177025.786 | 181451.4307 | 185987.7164 | 190637.4094 | 195403.3446 | 200288.4282 | 205295.6389 | 210428.0299 | 215688.7306 | 221080.9489 | 226607.9726
Net Economic Benefit |  | 5806578.4075

## Cost-Benefit (cost+30%)
VCR | 39440 |  | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
Discount Rate | 6.37%
Cost Sensitivity | 1.3
Do Nothing
Weighted EUSE (MWh) |  |  | 0.019566 | 0.019566 | 0.36982 | 3.1399 | 3.563 | 9.5522 | 22.1272 | 39.8817 | 104.1044 | 142.8741 | 142.8741 | 142.8741 | 142.8741 | 142.8741 | 142.8741
Weighted Cost of EUSE |  | 20066318.1693 | 771.6803 | 771.6803 | 14585.661 | 123838.7413 | 140524.8932 | 376738.0117 | 872697.1506 | 1572932.778 | 4105878.2237 | 5634952.985 | 5634952.985 | 5634952.985 | 5634952.985 | 5634952.985 | 5634952.985
Benefits |  | -20066318.1693 | -771.6803 | -771.6803 | -14585.661 | -123838.7413 | -140524.8932 | -376738.0117 | -872697.1506 | -1572932.778 | -4105878.2237 | -5634952.985 | -5634952.985 | -5634952.985 | -5634952.985 | -5634952.985 | -5634952.985
Costs |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Net Economic Benefit |  | -20066318.1693
Option 1
Weighted EUSE (MWh) |  |  | 0.019566 | 0.019566 | 0 | 0 | 0 | 4.9859e-05 | 0.00055085 | 0.0012561 | 0.0024538 | 0.0024538 | 0.0024538 | 0.0024538 | 0.0024538 | 0.0024538 | 0.0024538
Weighted Cost of EUSE |  | 1778.5295 | 771.6803 | 771.6803 | 0 | 0 | 0 | 1.9664 | 21.7256 | 49.5389 | 96.7788 | 96.7788 | 96.7788 | 96.7788 | 96.7788 | 96.7788 | 96.7788
Benefits |  | 20064539.6399 | 0 | 0 | 14585.661 | 123838.7413 | 140524.8932 | 376736.0452 | 872675.425 | 1572883.2391 | 4105781.4449 | 5634856.2062 | 5634856.2062 | 5634856.2062 | 5634856.2062 | 5634856.2062 | 5634856.2062
Costs |  | 18193031.5968 | 0 | 17870290.75 | 274755.7203 | 281624.6133 | 288665.2286 | 295881.8593 | 303278.9058 | 310860.8785 | 318632.4004 | 326598.2104 | 334763.1657 | 343132.2448 | 351710.551 | 360503.3147 | 369515.8976
Net Economic Benefit |  | 1871508.0431
Option 2
Weighted EUSE (MWh) |  |  | 0.019566 | 0.019566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Cost of EUSE |  | 1407.4911 | 771.6803 | 771.6803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Benefits |  | 20064910.6782 | 0 | 0 | 14585.661 | 123838.7413 | 140524.8932 | 376738.0117 | 872697.1506 | 1572932.778 | 4105878.2237 | 5634952.985 | 5634952.985 | 5634952.985 | 5634952.985 | 5634952.985 | 5634952.985
Costs |  | 21380011.8139 | 0 | 21000733 | 322886.2699 | 330958.4266 | 339232.3873 | 347713.197 | 356406.0269 | 365316.1776 | 374449.082 | 383810.3091 | 393405.5668 | 403240.706 | 413321.7236 | 423656.0667 | 434248.7558
Net Economic Benefit |  | -1315101.1356
Option 3
Weighted EUSE (MWh) |  |  | 0.019566 | 0.019566 | 47.2391 | 37.5363 | 61.7954 | 97.4041 | 121.4564 | 211.62 | 247.6341 | 247.6341 | 247.6341 | 247.6341 | 247.6341 | 247.6341 | 247.6341
Weighted Cost of EUSE |  | 48183320.7527 | 771.6803 | 771.6803 | 1863108.9243 | 1480432.2606 | 2437210.4809 | 3841617.7273 | 4790239.8771 | 8346293.5257 | 9766690.6328 | 9766690.6328 | 9766690.6328 | 9766690.6328 | 9766690.6328 | 9766690.6328 | 9766690.6328
Benefits |  | -28117002.5833 | 0 | 0 | -1848523.2633 | -1356593.5193 | -2296685.5877 | -3464879.7156 | -3917542.7265 | -6773360.7477 | -5660812.4091 | -4131737.6478 | -4131737.6478 | -4131737.6478 | -4131737.6478 | -4131737.6478 | -4131737.6478
Costs |  | 7850646.3158 | 0 | 7711377.375 | 118562.4271 | 121526.4878 | 124564.65 | 127678.7663 | 130870.7354 | 134142.5038 | 137496.0664 | 140933.4681 | 144456.8048 | 148068.2249 | 151769.9305 | 155564.1788 | 159453.2832
Net Economic Benefit |  | -35967648.8991
Option 4
Weighted EUSE (MWh) |  |  | 0.019566 | 0.019566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Cost of EUSE |  | 1407.4911 | 771.6803 | 771.6803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Benefits |  | 20064910.6782 | 0 | 0 | 14585.661 | 123838.7413 | 140524.8932 | 376738.0117 | 872697.1506 | 1572932.778 | 4105878.2237 | 5634952.985 | 5634952.985 | 5634952.985 | 5634952.985 | 5634952.985 | 5634952.985
Costs |  | 14504089.9256 | 0 | 14246790.1875 | 219044.3991 | 224520.5091 | 230133.5218 | 235886.8599 | 241784.0314 | 247828.6322 | 254024.348 | 260374.9567 | 266884.3306 | 273556.4389 | 280395.3498 | 287405.2336 | 294590.3644
Net Economic Benefit |  | 5560820.7527

## Cost-Benefit (cost-30%)
VCR | 39440 |  | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
Discount Rate | 6.37%
Cost Sensitivity | 0.7
Do Nothing
Weighted EUSE (MWh) |  |  | 0.019566 | 0.019566 | 0.36982 | 3.1399 | 3.563 | 9.5522 | 22.1272 | 39.8817 | 104.1044 | 142.8741 | 142.8741 | 142.8741 | 142.8741 | 142.8741 | 142.8741
Weighted Cost of EUSE |  | 20066318.1693 | 771.6803 | 771.6803 | 14585.661 | 123838.7413 | 140524.8932 | 376738.0117 | 872697.1506 | 1572932.778 | 4105878.2237 | 5634952.985 | 5634952.985 | 5634952.985 | 5634952.985 | 5634952.985 | 5634952.985
Benefits |  | -20066318.1693 | -771.6803 | -771.6803 | -14585.661 | -123838.7413 | -140524.8932 | -376738.0117 | -872697.1506 | -1572932.778 | -4105878.2237 | -5634952.985 | -5634952.985 | -5634952.985 | -5634952.985 | -5634952.985 | -5634952.985
Costs |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Net Economic Benefit |  | -20066318.1693
Option 1
Weighted EUSE (MWh) |  |  | 0.019566 | 0.019566 | 0 | 0 | 0 | 4.9859e-05 | 0.00055085 | 0.0012561 | 0.0024538 | 0.0024538 | 0.0024538 | 0.0024538 | 0.0024538 | 0.0024538 | 0.0024538
Weighted Cost of EUSE |  | 1778.5295 | 771.6803 | 771.6803 | 0 | 0 | 0 | 1.9664 | 21.7256 | 49.5389 | 96.7788 | 96.7788 | 96.7788 | 96.7788 | 96.7788 | 96.7788 | 96.7788
Benefits |  | 20064539.6399 | 0 | 0 | 14585.661 | 123838.7413 | 140524.8932 | 376736.0452 | 872675.425 | 1572883.2391 | 4105781.4449 | 5634856.2062 | 5634856.2062 | 5634856.2062 | 5634856.2062 | 5634856.2062 | 5634856.2062
Costs |  | 9796247.7829 | 0 | 9622464.25 | 147945.3878 | 151644.0225 | 155435.1231 | 159321.0012 | 163304.0262 | 167386.6269 | 171571.2925 | 175860.5749 | 180257.0892 | 184763.5165 | 189382.6044 | 194117.1695 | 198970.0987
Net Economic Benefit |  | 10268291.857
Option 2
Weighted EUSE (MWh) |  |  | 0.019566 | 0.019566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Cost of EUSE |  | 1407.4911 | 771.6803 | 771.6803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Benefits |  | 20064910.6782 | 0 | 0 | 14585.661 | 123838.7413 | 140524.8932 | 376738.0117 | 872697.1506 | 1572932.778 | 4105878.2237 | 5634952.985 | 5634952.985 | 5634952.985 | 5634952.985 | 5634952.985 | 5634952.985
Costs |  | 11512314.0536 | 0 | 11308087 | 173861.8376 | 178208.3836 | 182663.5932 | 187230.183 | 191910.9376 | 196708.711 | 201626.4288 | 206667.0895 | 211833.7667 | 217129.6109 | 222557.8512 | 228122.4974 | 233826.2531
Net Economic Benefit |  | 8552596.6246
Option 3
Weighted EUSE (MWh) |  |  | 0.019566 | 0.019566 | 47.2391 | 37.5363 | 61.7954 | 97.4041 | 121.4564 | 211.62 | 247.6341 | 247.6341 | 247.6341 | 247.6341 | 247.6341 | 247.6341 | 247.6341
Weighted Cost of EUSE |  | 48183320.7527 | 771.6803 | 771.6803 | 1863108.9243 | 1480432.2606 | 2437210.4809 | 3841617.7273 | 4790239.8771 | 8346293.5257 | 9766690.6328 | 9766690.6328 | 9766690.6328 | 9766690.6328 | 9766690.6328 | 9766690.6328 | 9766690.6328
Benefits |  | -28117002.5833 | 0 | 0 | -1848523.2633 | -1356593.5193 | -2296685.5877 | -3464879.7156 | -3917542.7265 | -6773360.7477 | -5660812.4091 | -4131737.6478 | -4131737.6478 | -4131737.6478 | -4131737.6478 | -4131737.6478 | -4131737.6478
Costs |  | 4227271.0931 | 0 | 4152280.125 | 63841.3069 | 65437.3396 | 67073.2731 | 68750.1049 | 70468.8575 | 72230.579 | 74036.3434 | 75887.252 | 77784.4333 | 79729.0442 | 81722.2703 | 83765.327 | 85859.4602
Net Economic Benefit |  | -32344273.6764
Option 4
Weighted EUSE (MWh) |  |  | 0.019566 | 0.019566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Cost of EUSE |  | 1407.4911 | 771.6803 | 771.6803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Benefits |  | 20064910.6782 | 0 | 0 | 14585.661 | 123838.7413 | 140524.8932 | 376738.0117 | 872697.1506 | 1572932.778 | 4105878.2237 | 5634952.985 | 5634952.985 | 5634952.985 | 5634952.985 | 5634952.985 | 5634952.985
Costs |  | 7809894.5753 | 0 | 7671348.5625 | 117946.9841 | 120895.6588 | 123918.0502 | 127016.0015 | 130191.4015 | 133446.1866 | 136782.3412 | 140201.8997 | 143706.9472 | 147299.6209 | 150982.1114 | 154756.6642 | 158625.5808
Net Economic Benefit |  | 12255016.1029